## PF, THD, EFF
EFFICIENCY, PF, and THD
DER-925 Unit 9
| WITH DAUGHTER BOARD | [12 empty] | NO DAUGHTER BOARD
| LOAD: 48V LED Load | [12 empty] | LOAD: 48V LED Load
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency
| 90 | 60 | 89.85 | 470.99 | 42.013 | 0.9928 | 6.623 | 47.573 | 772.1 | 36.739 | -1.0128 | 87.4467
| 100 | 60 | 99.89 | 419.34 | 41.683 | 0.9951 | 4.106 | 47.532 | 772.2 | 36.709 | -1 | 88.0671
| 110 | 60 | 109.84 | 379.83 | 41.485 | 0.9944 | 4.004 | 47.497 | 772.1 | 36.682 | -1.0128 | 88.4223
| 115 | 60 | 114.9 | 363.01 | 41.422 | 0.993 | 4.123 | 47.465 | 772.3 | 36.661 | -0.98718 | 88.5061
| 120 | 60 | 119.87 | 347.66 | 41.345 | 0.9922 | 4.353 | 47.44 | 772.6 | 36.661 | -0.94872 | 88.6709
| 132 | 60 | 131.88 | 315.71 | 41.208 | 0.9898 | 4.052 | 47.412 | 772.5 | 36.633 | -0.96154 | 88.8978
| 180 | 50 | 179.87 | 233.03 | 41.006 | 0.9782 | 5.471 | 47.392 | 772.7 | 36.627 | -0.9359 | 89.3211
| 200 | 50 | 199.93 | 211.18 | 40.96 | 0.9703 | 5.834 | 47.369 | 772.7 | 36.609 | -0.9359 | 89.3774
| 230 | 50 | 229.93 | 186.68 | 40.96 | 0.9542 | 6.779 | 47.354 | 772.7 | 36.6 | -0.9359 | 89.3555
| 265 | 50 | 264.92 | 166.48 | 40.99 | 0.9295 | 8.266 | 47.333 | 772.8 | 36.585 | -0.92308 | 89.2535
| 277 | 60 | 276.94 | 164.24 | 41.01 | 0.9017 | 9.202 | 47.315 | 772.9 | 36.579 | -0.91026 | 89.1953
| 300 | 60 | 299.92 | 156.1 | 41.04 | 0.8767 | 10.775 | 47.302 | 772.9 | 36.565 | -0.91026 | 89.096
| LOAD: 36V LED Load | [12 empty] | LOAD: 36V LED Load
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency
| 90 | 60 | 89.87 | 353.45 | 31.575 | 0.994 | 4.051 | 35.739 | 772.1 | 27.6 | -1.0128 | 87.4109
| 100 | 60 | 99.91 | 316.65 | 31.421 | 0.9932 | 4.143 | 35.723 | 772 | 27.585 | -1.0256 | 87.7916
| 110 | 60 | 109.86 | 287.55 | 31.312 | 0.9912 | 4.024 | 35.71 | 772 | 27.573 | -1.0256 | 88.0589
| 115 | 60 | 114.92 | 274.84 | 31.271 | 0.99 | 4.029 | 35.701 | 772.1 | 27.57 | -1.0128 | 88.1648
| 120 | 60 | 119.89 | 263.65 | 31.237 | 0.9882 | 3.866 | 35.691 | 772.1 | 27.561 | -1.0128 | 88.2319
| 132 | 60 | 131.89 | 240.02 | 31.162 | 0.9844 | 4.126 | 35.683 | 772.1 | 27.557 | -1.0128 | 88.4314
| 180 | 50 | 179.88 | 178.42 | 31.013 | 0.9663 | 6.195 | 35.671 | 770.6 | 27.494 | -1.2051 | 88.6531
| 200 | 50 | 199.94 | 162.69 | 31.01 | 0.9535 | 6.902 | 35.665 | 770.6 | 27.488 | -1.2051 | 88.6424
| 230 | 50 | 229.87 | 145.26 | 31.043 | 0.9297 | 8.247 | 35.658 | 770.5 | 27.481 | -1.2179 | 88.5256
| 265 | 50 | 264.87 | 131.44 | 31.112 | 0.8937 | 10.222 | 35.655 | 770.6 | 27.48 | -1.2051 | 88.326
| 277 | 60 | 276.89 | 131.81 | 31.189 | 0.8546 | 11.991 | 35.655 | 771.9 | 27.527 | -1.0385 | 88.2587
| 300 | 60 | 299.87 | 126.83 | 31.247 | 0.8215 | 13.776 | 35.65 | 771.8 | 27.519 | -1.0513 | 88.0693
| LOAD: 24V LED Load | [12 empty] | LOAD: 24V LED Load
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement |  |  |  |  | Remarks
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %V Reg | Efficiency
| 90 | 60 | 89.77 | 240.84 | 21.332 | 0.9866 | 6.811 | 23.871 | 771 | 18.409 | -1.1538 | 86.2976
| 100 | 60 | 99.82 | 215.46 | 21.261 | 0.9885 | 4.46 | 23.873 | 771.6 | 18.424 | -1.0769 | 86.6563
| 110 | 60 | 109.78 | 196.27 | 21.215 | 0.9846 | 5.154 | 23.874 | 771.4 | 18.421 | -1.1026 | 86.8301
| 115 | 60 | 114.84 | 188.04 | 21.209 | 0.9822 | 5.337 | 23.874 | 771.6 | 18.425 | -1.0769 | 86.8735
| 120 | 60 | 119.82 | 180.43 | 21.195 | 0.9804 | 4.981 | 23.873 | 771.6 | 18.424 | -1.0769 | 86.9262
| 132 | 60 | 131.82 | 165.11 | 21.174 | 0.9728 | 6.021 | 23.874 | 771.4 | 18.421 | -1.1026 | 86.9982
| 180 | 50 | 179.83 | 125.33 | 21.168 | 0.9391 | 9.085 | 23.873 | 770.5 | 18.397 | -1.2179 | 86.9095
| 200 | 50 | 199.89 | 115.62 | 21.193 | 0.917 | 9.908 | 23.874 | 770.4 | 18.396 | -1.2308 | 86.8022
| 230 | 50 | 229.9 | 105.43 | 21.25 | 0.8767 | 12.13 | 23.873 | 770.3 | 18.392 | -1.2436 | 86.5506
| 265 | 50 | 264.9 | 97.9 | 21.332 | 0.8226 | 14.924 | 23.873 | 769.9 | 18.384 | -1.2949 | 86.1804
| 277 | 60 | 276.92 | 100.29 | 21.38 | 0.7698 | 16.973 | 23.875 | 771 | 18.41 | -1.1538 | 86.1085
| 300 | 60 | 299.89 | 98.09 | 21.439 | 0.7288 | 19.14 | 23.875 | 770.8 | 18.407 | -1.1795 | 85.8575
|  | 5% | -5% | [11 empty] | 3% | -3%
| 90 | 808.5 | 731.5 | [10 empty] | 90 | 793 | 747
| 100 | 808.5 | 731.5 | [10 empty] | 100 | 793 | 747
| 110 | 808.5 | 731.5 | [10 empty] | 110 | 793 | 747
| 115 | 808.5 | 731.5 | [10 empty] | 115 | 793 | 747
| 120 | 808.5 | 731.5 | [10 empty] | 120 | 793 | 747
| 132 | 808.5 | 731.5 | [10 empty] | 132 | 793 | 747
| 180 | 808.5 | 731.5 | [10 empty] | 180 | 793 | 747
| 200 | 808.5 | 731.5 | [10 empty] | 200 | 793 | 747
| 230 | 808.5 | 731.5 | [10 empty] | 230 | 793 | 747
| 265 | 808.5 | 731.5 | [10 empty] | 265 | 793 | 747
| 277 | 808.5 | 731.5 | [10 empty] | 277 | 793 | 747
| 300 | 808.5 | 731.5 | [10 empty] | 300 | 793 | 747

## Harmonics
Current Harmonics
DER-925 Unit 9
| HARMONICS: 120 VAC, 48V LED Load | [11 empty] | HARMONICS: 120 VAC, 36V LED Load | [11 empty] | HARMONICS: 120 VAC, 24V LED Load
| 120 | 60 | 119.89 | 347.42 | 41.323 | 0.9921 | 3.459 | 47.9 | 765.6 | 36.64 | -1.8462 | 88.6673 | 120 | 60 | 119.91 | 264.54 | 31.317 | 0.9873 | 3.555 | 36.175 | 766.4 | 27.698 | -1.7436 | 88.444 | 120 | 60 | 119.83 | 178.86 | 20.917 | 0.9759 | 5.471 | 23.83 | 765.7 | 18.228 | -1.8333 | 87.1444
| nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks
| 1 | 346.71 | [10 empty] | 1 | 263.7 | [10 empty] | 1 | 177.51
| 2 | 0.29 | 0.083643 |  | 2 | pass | [6 empty] | 2 | 0.11 | 0.041714 |  | 2 | pass | [6 empty] | 2 | 0.12 | 0.067602 |  | 2
| 3 | 9.29 | 2.6795 | 140.4982 | 29.763 | pass | [6 empty] | 3 | 8.2 | 3.1096 | 106.4778 | 29.619 | pass | [6 empty] | 3 | 7.97 | 4.4899 | 71.1178 | 29.277 | pass
| 5 | 1.21 | 0.34899 | 78.5137 | 10 | pass | [6 empty] | 5 | 0.56 | 0.21236 | 59.5023 | 10 | pass | [6 empty] | 5 | 1.06 | 0.59715 | 39.7423 | 10 | pass
| 7 | 1.53 | 0.44129 | 41.323 | 7 | pass | [6 empty] | 7 | 0.82 | 0.31096 | 31.317 | 7 | pass | [6 empty] | 7 | 0.68 | 0.38308 | 20.917 | 7 | pass
| 9 | 1.63 | 0.47013 | 20.6615 | 5 | pass | [6 empty] | 9 | 1.28 | 0.4854 | 15.6585 | 5 | pass | [6 empty] | 9 | 1.11 | 0.62532 | 10.4585 | 5 | pass
| 11 | 0.49 | 0.14133 | 14.4631 | 3 | pass | [6 empty] | 11 | 0.47 | 0.17823 | 10.961 | 3 | pass | [6 empty] | 11 | 1.95 | 1.0985 | 7.3209 | 3 | pass
| 13 | 1.56 | 0.44994 | 12.238 | 3 | pass | [6 empty] | 13 | 0.92 | 0.34888 | 9.2746 | 3 | pass | [6 empty] | 13 | 0.25 | 0.14084 | 6.1947 | 3 | pass
| 15 | 1.28 | 0.36918 | 10.6062 | 3 | pass | [6 empty] | 15 | 0.34 | 0.12893 | 8.038 | 3 | pass | [6 empty] | 15 | 1.23 | 0.69292 | 5.3687 | 3 | pass
| 17 | 0.61 | 0.17594 | 9.3584 | 3 | pass | [6 empty] | 17 | 1.36 | 0.51574 | 7.0924 | 3 | pass | [6 empty] | 17 | 0.22 | 0.12394 | 4.7371 | 3 | pass
| 19 | 1.23 | 0.35476 | 8.3733 | 3 | pass | [6 empty] | 19 | 0.33 | 0.12514 | 6.3458 | 3 | pass | [6 empty] | 19 | 0.87 | 0.49011 | 4.2384 | 3 | pass
| 21 | 0.22 | 0.063454 | 7.5759 | 3 | pass | [6 empty] | 21 | 1.27 | 0.48161 | 5.7415 | 3 | pass | [6 empty] | 21 | 0.11 | 0.061968 | 3.8348 | 3 | pass
| 23 | 3.03 | 0.87393 | 6.9171 | 3 | pass | [6 empty] | 23 | 1.04 | 0.39439 | 5.2422 | 3 | pass | [6 empty] | 23 | 0.82 | 0.46195 | 3.5013 | 3 | pass
| 25 | 0.74 | 0.21343 | 6.3637 | 3 | pass | [6 empty] | 25 | 0.85 | 0.32234 | 4.8228 | 3 | pass | [6 empty] | 25 | 0.65 | 0.36618 | 3.2212 | 3 | pass
| 27 | 2.28 | 0.65761 | 5.8924 | 3 | pass | [6 empty] | 27 | 1.27 | 0.48161 | 4.4656 | 3 | pass | [6 empty] | 27 | 0.72 | 0.40561 | 2.9826 | 3 | pass
| 29 | 2.49 | 0.71818 | 5.486 | 3 | pass | [6 empty] | 29 | 0.27 | 0.10239 | 4.1576 | 3 | pass | [6 empty] | 29 | 0.2 | 0.11267 | 2.7769 | 3 | pass
| 31 | 2.31 | 0.66626 | 5.132 | 3 | pass | [6 empty] | 31 | 1.36 | 0.51574 | 3.8894 | 3 | pass | [6 empty] | 31 | 0.74 | 0.41688 | 2.5978 | 3 | pass
| 33 | 1.29 | 0.37207 | 4.821 | 3 | pass | [6 empty] | 33 | 1.41 | 0.5347 | 3.6536 | 3 | pass | [6 empty] | 33 | 0.7 | 0.39434 | 2.4403 | 3 | pass
| 35 | 2.62 | 0.75567 | 4.5455 | 3 | pass | [6 empty] | 35 | 0.99 | 0.37543 | 3.4449 | 3 | pass | [6 empty] | 35 | 1.7 | 0.95769 | 2.3009 | 3 | pass
| 37 | 0.43 | 0.12402 | 4.2998 | 3 | pass | [6 empty] | 37 | 0.95 | 0.36026 | 3.2587 | 3 | pass | [6 empty] | 37 | 0.45 | 0.25351 | 2.1765 | 3 | pass
| 39 | 1.69 | 0.48744 | 4.0793 | 3 | pass | [6 empty] | 39 | 0.89 | 0.3375 | 3.0915 | 3 | pass | [6 empty] | 39 | 1 | 0.56335 | 2.0649 | 3 | pass
| 41 | 1.34 | 0.38649 | 3.8803 | 3 | pass | [6 empty] | 41 | 0.88 | 0.33371 | 2.9407 | 3 | pass | [6 empty] | 41 | 0.39 | 0.21971 | 1.9642 | 3 | pass
| HARMONICS: 230 VAC, 48V LED Load | [11 empty] | HARMONICS: 230 VAC, 36V LED Load | [11 empty] | HARMONICS: 230 VAC, 24V LED Load
| 230 | 50 | 229.85 | 186.05 | 40.783 | 0.9536 | 6.852 | 47.902 | 766.1 | 36.658 | -1.7821 | 89.8855 | 230 | 50 | 229.88 | 145.34 | 31 | 0.9278 | 8.314 | 36.172 | 765.9 | 27.678 | -1.8077 | 89.2839 | 230 | 50 | 229.91 | 104.71 | 20.934 | 0.8695 | 12.301 | 23.919 | 765.4 | 18.288 | -1.8718 | 87.3603
| nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks
| 1 | 184.6 | [10 empty] | 1 | 143.84 | [10 empty] | 1 | 102.31
| 2 | 0.38 | 0.20585 |  | 2 | pass | [6 empty] | 2 | 0.15 | 0.10428 |  | 2 | pass | [6 empty] | 2 | 0.2 | 0.19548 |  | 2
| 3 | 11.02 | 5.9697 | 138.6622 | 28.608 | pass | [6 empty] | 3 | 10.14 | 7.0495 | 105.4 | 27.834 | pass | [6 empty] | 3 | 10.71 | 10.4682 | 71.1756 | 26.085 | pass
| 5 | 1.66 | 0.89924 | 77.4877 | 10 | pass | [6 empty] | 5 | 1.87 | 1.3001 | 58.9 | 10 | pass | [6 empty] | 5 | 3.03 | 2.9616 | 39.7746 | 10 | pass
| 7 | 1.69 | 0.91549 | 40.783 | 7 | pass | [6 empty] | 7 | 2.13 | 1.4808 | 31 | 7 | pass | [6 empty] | 7 | 2.62 | 2.5608 | 20.934 | 7 | pass
| 9 | 1.48 | 0.80173 | 20.3915 | 5 | pass | [6 empty] | 9 | 2.04 | 1.4182 | 15.5 | 5 | pass | [6 empty] | 9 | 2.6 | 2.5413 | 10.467 | 5 | pass
| 11 | 1.74 | 0.94258 | 14.2741 | 3 | pass | [6 empty] | 11 | 1.78 | 1.2375 | 10.85 | 3 | pass | [6 empty] | 11 | 2.05 | 2.0037 | 7.3269 | 3 | pass
| 13 | 1.06 | 0.57421 | 12.078 | 3 | pass | [6 empty] | 13 | 1.71 | 1.1888 | 9.1808 | 3 | pass | [6 empty] | 13 | 1.93 | 1.8864 | 6.1997 | 3 | pass
| 15 | 1.77 | 0.95883 | 10.4676 | 3 | pass | [6 empty] | 15 | 1.74 | 1.2097 | 7.9567 | 3 | pass | [6 empty] | 15 | 1.52 | 1.4857 | 5.3731 | 3 | pass
| 17 | 1.16 | 0.62839 | 9.2362 | 3 | pass | [6 empty] | 17 | 1.49 | 1.0359 | 7.0206 | 3 | pass | [6 empty] | 17 | 1.29 | 1.2609 | 4.7409 | 3 | pass
| 19 | 1.48 | 0.80173 | 8.2639 | 3 | pass | [6 empty] | 19 | 1.3 | 0.90378 | 6.2816 | 3 | pass | [6 empty] | 19 | 0.93 | 0.909 | 4.2419 | 3 | pass
| 21 | 0.94 | 0.50921 | 7.4769 | 3 | pass | [6 empty] | 21 | 1.14 | 0.79255 | 5.6833 | 3 | pass | [6 empty] | 21 | 0.89 | 0.86991 | 3.8379 | 3 | pass
| 23 | 1.33 | 0.72048 | 6.8267 | 3 | pass | [6 empty] | 23 | 1.02 | 0.70912 | 5.1891 | 3 | pass | [6 empty] | 23 | 0.93 | 0.909 | 3.5042 | 3 | pass
| 25 | 0.56 | 0.30336 | 6.2806 | 3 | pass | [6 empty] | 25 | 0.67 | 0.4658 | 4.774 | 3 | pass | [6 empty] | 25 | 0.71 | 0.69397 | 3.2238 | 3 | pass
| 27 | 1.27 | 0.68797 | 5.8154 | 3 | pass | [6 empty] | 27 | 0.64 | 0.44494 | 4.4204 | 3 | pass | [6 empty] | 27 | 0.89 | 0.86991 | 2.985 | 3 | pass
| 29 | 0.61 | 0.33044 | 5.4143 | 3 | pass | [6 empty] | 29 | 0.37 | 0.25723 | 4.1155 | 3 | pass | [6 empty] | 29 | 0.68 | 0.66465 | 2.7792 | 3 | pass
| 31 | 1.28 | 0.69339 | 5.065 | 3 | pass | [6 empty] | 31 | 0.38 | 0.26418 | 3.85 | 3 | pass | [6 empty] | 31 | 0.8 | 0.78194 | 2.5999 | 3 | pass
| 33 | 1.51 | 0.81798 | 4.758 | 3 | pass | [6 empty] | 33 | 0.76 | 0.52836 | 3.6167 | 3 | pass | [6 empty] | 33 | 0.5 | 0.48871 | 2.4423 | 3 | pass
| 35 | 0.85 | 0.46046 | 4.4861 | 3 | pass | [6 empty] | 35 | 1.59 | 1.1054 | 3.41 | 3 | pass | [6 empty] | 35 | 0.74 | 0.72329 | 2.3027 | 3 | pass
| 37 | 0.9 | 0.48754 | 4.2436 | 3 | pass | [6 empty] | 37 | 0.18 | 0.12514 | 3.2257 | 3 | pass | [6 empty] | 37 | 0.46 | 0.44961 | 2.1783 | 3 | pass
| 39 | 1.16 | 0.62839 | 4.026 | 3 | pass | [6 empty] | 39 | 0.46 | 0.3198 | 3.0603 | 3 | pass | [6 empty] | 39 | 0.74 | 0.72329 | 2.0666 | 3 | pass
| 41 | 1.7 | 0.92091 | 3.8296 | 3 | pass | [6 empty] | 41 | 0.47 | 0.32675 | 2.911 | 3 | pass | [6 empty] | 41 | 0.3 | 0.29323 | 1.9658 | 3 | pass
| HARMONICS: 277 VAC, 48V LED Load | [11 empty] | HARMONICS: 277 VAC, 36V LED Load | [11 empty] | HARMONICS: 277 VAC, 24V LED Load
| 277 | 60 | 276.89 | 163.15 | 40.77 | 0.9025 | 9.033 | 47.913 | 766.3 | 36.683 | -1.7564 | 89.9755 | 277 | 60 | 276.91 | 131.39 | 31.064 | 0.8538 | 11.75 | 36.174 | 767.1 | 27.723 | -1.6538 | 89.2448 | 277 | 60 | 276.94 | 99.21 | 20.968 | 0.7632 | 17.067 | 23.913 | 766.5 | 18.31 | -1.7308 | 87.3235
| nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks | [6 empty] | nth order | mA content | % content | mA Limit <25W | % limit, >25W | Remarks
| 1 | 161.53 | [10 empty] | 1 | 129.01 | [10 empty] | 1 | 96.21
| 2 | 0.06 | 0.037145 |  | 2 | pass | [6 empty] | 2 | 0.1 | 0.077513 |  | 2 | pass | [6 empty] | 2 | 0.17 | 0.1767 |  | 2
| 3 | 11.12 | 6.8842 | 138.618 | 27.075 | pass | [6 empty] | 3 | 11.44 | 8.8675 | 105.6176 | 25.614 | pass | [6 empty] | 3 | 12.39 | 12.8781 | 71.2912 | 22.896 | pass
| 5 | 3.74 | 2.3154 | 77.463 | 10 | pass | [6 empty] | 5 | 4.71 | 3.6509 | 59.0216 | 10 | pass | [6 empty] | 5 | 6.69 | 6.9535 | 39.8392 | 10 | pass
| 7 | 3.85 | 2.3835 | 40.77 | 7 | pass | [6 empty] | 7 | 4.42 | 3.4261 | 31.064 | 7 | pass | [6 empty] | 7 | 4.68 | 4.8644 | 20.968 | 7 | pass
| 9 | 3.57 | 2.2101 | 20.385 | 5 | pass | [6 empty] | 9 | 3.98 | 3.085 | 15.532 | 5 | pass | [6 empty] | 9 | 3.43 | 3.5651 | 10.484 | 5 | pass
| 11 | 2.66 | 1.6468 | 14.2695 | 3 | pass | [6 empty] | 11 | 2.74 | 2.1239 | 10.8724 | 3 | pass | [6 empty] | 11 | 2.54 | 2.6401 | 7.3388 | 3 | pass
| 13 | 2.47 | 1.5291 | 12.0742 | 3 | pass | [6 empty] | 13 | 2.41 | 1.8681 | 9.1997 | 3 | pass | [6 empty] | 13 | 1.95 | 2.0268 | 6.2098 | 3 | pass
| 15 | 2.58 | 1.5972 | 10.4643 | 3 | pass | [6 empty] | 15 | 2.06 | 1.5968 | 7.9731 | 3 | pass | [6 empty] | 15 | 2.03 | 2.11 | 5.3818 | 3 | pass
| 17 | 2.6 | 1.6096 | 9.2332 | 3 | pass | [6 empty] | 17 | 1.68 | 1.3022 | 7.0351 | 3 | pass | [6 empty] | 17 | 2.47 | 2.5673 | 4.7486 | 3 | pass
| 19 | 1.44 | 0.89148 | 8.2613 | 3 | pass | [6 empty] | 19 | 1.51 | 1.1705 | 6.2945 | 3 | pass | [6 empty] | 19 | 1.7 | 1.767 | 4.2488 | 3 | pass
| 21 | 1.21 | 0.74909 | 7.4745 | 3 | pass | [6 empty] | 21 | 1.6 | 1.2402 | 5.6951 | 3 | pass | [6 empty] | 21 | 1.2 | 1.2473 | 3.8441 | 3 | pass
| 23 | 1.1 | 0.68099 | 6.8245 | 3 | pass | [6 empty] | 23 | 1.41 | 1.0929 | 5.1998 | 3 | pass | [6 empty] | 23 | 1.37 | 1.424 | 3.5099 | 3 | pass
| 25 | 0.95 | 0.58813 | 6.2786 | 3 | pass | [6 empty] | 25 | 1.02 | 0.79064 | 4.7839 | 3 | pass | [6 empty] | 25 | 1.17 | 1.2161 | 3.2291 | 3 | pass
| 27 | 1.06 | 0.65622 | 5.8135 | 3 | pass | [6 empty] | 27 | 1.24 | 0.96117 | 4.4295 | 3 | pass | [6 empty] | 27 | 1.22 | 1.2681 | 2.9899 | 3 | pass
| 29 | 0.86 | 0.53241 | 5.4126 | 3 | pass | [6 empty] | 29 | 1.06 | 0.82164 | 4.124 | 3 | pass | [6 empty] | 29 | 0.84 | 0.87309 | 2.7837 | 3 | pass
| 31 | 1.1 | 0.68099 | 5.0634 | 3 | pass | [6 empty] | 31 | 1.09 | 0.8449 | 3.8579 | 3 | pass | [6 empty] | 31 | 1 | 1.0394 | 2.6041 | 3 | pass
| 33 | 1.1 | 0.68099 | 4.7565 | 3 | pass | [6 empty] | 33 | 1 | 0.77513 | 3.6241 | 3 | pass | [6 empty] | 33 | 0.87 | 0.90427 | 2.4463 | 3 | pass
| 35 | 1.02 | 0.63146 | 4.4847 | 3 | pass | [6 empty] | 35 | 0.87 | 0.67437 | 3.417 | 3 | pass | [6 empty] | 35 | 0.81 | 0.84191 | 2.3065 | 3 | pass
| 37 | 0.8 | 0.49526 | 4.2423 | 3 | pass | [6 empty] | 37 | 0.75 | 0.58135 | 3.2323 | 3 | pass | [6 empty] | 37 | 0.9 | 0.93545 | 2.1818 | 3 | pass
| 39 | 1 | 0.61908 | 4.0247 | 3 | pass | [6 empty] | 39 | 0.98 | 0.75963 | 3.0666 | 3 | pass | [6 empty] | 39 | 0.77 | 0.80033 | 2.0699 | 3 | pass
| 41 | 0.52 | 0.32192 | 3.8284 | 3 | pass | [6 empty] | 41 | 0.57 | 0.44183 | 2.917 | 3 | pass | [6 empty] | 41 | 0.95 | 0.98742 | 1.9689 | 3 | pass

## No Load Input Power
No Load Input Power
DER-925 Unit 9
NO LOAD INPUT POWER
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 90 | 60 | 89.93 | 19.201 | 0.41763 | 0.2426 |  | 52.268 | 0.0001 | 1e-05 | -100 | 0.0023945
| 100 | 60 | 99.95 | 20.333 | 0.50712 | 0.2501 |  | 52.277 | 0.0001 | 1e-05 | -100 | 0.0019719
| 110 | 60 | 109.89 | 20.804 | 0.52023 | 0.2274 |  | 52.276 | 0.0003 | 1e-05 | -100 | 0.0019222
| 115 | 60 | 114.96 | 20.853 | 0.49542 | 0.2077 |  | 52.273 | 0.0001 | 0 | -100 | 0
| 120 | 60 | 119.93 | 20.934 | 0.47664 | 0.1918 |  | 52.267 | 0 | 0 | -100 | 0
| 132 | 60 | 131.92 | 21.297 | 0.4431 | 0.1584 |  | 52.265 | 0.0001 | 0 | -100 | 0
| 180 | 50 | 179.88 | 21.677 | 0.38142 | 0.0986 |  | 52.257 | 0 | 0 | -100 | 0
| 200 | 50 | 199.69 | 22.95 | 0.36858 | 0.0802 |  | 52.257 | 0.0002 | 1e-05 | -100 | 0.0027131
| 230 | 50 | 229.84 | 25.152 | 0.35721 | 0.062 |  | 52.256 | 0.0001 | 1e-05 | -100 | 0.0027995
| 265 | 50 | 264.65 | 27.759 | 0.35166 | 0.0485 |  | 52.255 | 0.0001 | 0 | -100 | 0
| 277 | 60 | 276.56 | 32.893 | 0.35187 | 0.0381 |  | 52.252 | 0 | 0 | -100 | 0
| 300 | 60 | 299.93 | 34.85 | 0.35445 | 0.0336 |  | 52.254 | 0.0001 | 1e-05 | -100 | 0.0028213
LIGHT OFF INPUT POWER
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 90 | 60 | 89.93 | 16.343 | 0.057495 | 0.0389 |  | 17.482 | 0.0008 | 1.4e-05 | -99.9999 | 0.02435
| 100 | 60 | 99.9 | 16.994 | 0.05781 | 0.0343 |  | 17.481 | 0.0008 | 1.4e-05 | -99.9999 | 0.024217
| 110 | 60 | 109.83 | 17.677 | 0.059745 | 0.03 |  | 17.483 | 0.0009 | 1.5e-05 | -99.9999 | 0.025107
| 115 | 60 | 114.96 | 18.032 | 0.061929 | 0.0301 |  | 17.483 | 0.0008 | 1.4e-05 | -99.9999 | 0.022607
| 120 | 60 | 119.92 | 18.41 | 0.064506 | 0.0295 |  | 17.483 | 0.0009 | 1.5e-05 | -99.9999 | 0.023254
| 132 | 60 | 131.86 | 19.283 | 0.071199 | 0.0284 |  | 17.487 | 0.0008 | 1.3e-05 | -99.9999 | 0.018259
| 180 | 50 | 179.78 | 20.721 | 0.10453 | 0.0276 |  | 17.515 | 0.0009 | 1.6e-05 | -99.9999 | 0.015307
| 200 | 50 | 199.95 | 22.244 | 0.12123 | 0.0274 |  | 17.52 | 0.0013 | 2.2e-05 | -99.9998 | 0.018148
| 230 | 50 | 229.93 | 24.672 | 0.14784 | 0.026 |  | 17.524 | 0.0014 | 2.4e-05 | -99.9998 | 0.016234
| 265 | 50 | 264.81 | 27.43 | 0.18257 | 0.025 |  | 17.528 | 0.0014 | 2.5e-05 | -99.9998 | 0.013693
| 277 | 60 | 276.81 | 32.641 | 0.19661 | 0.0219 |  | 17.527 | 0.0014 | 2.5e-05 | -99.9998 | 0.012716
| 300 | 60 | 299.91 | 34.66 | 0.22282 | 0.0215 |  | 17.529 | 0.0014 | 2.5e-05 | -99.9998 | 0.01122

## Analog Dimming
Legacy Dimming: Analog
DER-925 Unit 9
| 48V LED, 120 VAC | [12 empty] | 48V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 36V LED, 120 VAC | [12 empty] | 36V LED, 230 VAC | [12 empty] | 36V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
|  | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
|  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 10 | 120 | 60 | 119.85 | 347.84 | 41.365 | 0.9922 | 4.178 | 47.536 | 771.5 | 36.683 | -1.0897 | 88.6813 | 10 | 230 | 50 | 229.8 | 187.36 | 41.114 | 0.9549 | 7.091 | 47.603 | 772.3 | 36.77 | -0.98718 | 89.4343 | 10 | 277 | 60 | 276.82 | 164.79 | 41.185 | 0.9029 | 9.319 | 47.591 | 772.6 | 36.775 | -0.94872 | 89.2922 | 10 | 120 | 60 | 119.87 | 264.36 | 31.315 | 0.9882 | 3.823 | 35.771 | 772.5 | 27.638 | -0.96154 | 88.258 | 10 | 230 | 50 | 229.85 | 145.62 | 31.126 | 0.9299 | 8.336 | 35.751 | 770.9 | 27.563 | -1.1667 | 88.553 | 10 | 277 | 60 | 276.88 | 131.65 | 31.145 | 0.8544 | 12.207 | 35.632 | 771.6 | 27.498 | -1.0769 | 88.2903 | 10 | 120 | 60 | 119.82 | 179.78 | 21.114 | 0.9803 | 4.707 | 23.818 | 770.8 | 18.363 | -1.1795 | 86.9707 | 10 | 230 | 50 | 229.89 | 105.11 | 21.167 | 0.876 | 12.293 | 23.824 | 769.5 | 18.336 | -1.3462 | 86.6254 | 10 | 277 | 60 | 276.9 | 100.04 | 21.303 | 0.769 | 16.885 | 23.824 | 770.3 | 18.355 | -1.2436 | 86.1616
| 9 | 120 | 60 | 119.85 | 347.59 | 41.337 | 0.9922 | 4.282 | 47.513 | 771.6 | 36.665 | -1.0769 | 88.6978 | 9 | 230 | 50 | 229.8 | 187.23 | 41.084 | 0.9549 | 6.876 | 47.573 | 772.2 | 36.741 | -1 | 89.429 | 9 | 277 | 60 | 276.82 | 164.68 | 41.154 | 0.9028 | 9.482 | 47.561 | 772.4 | 36.745 | -0.97436 | 89.2866 | 9 | 120 | 60 | 119.87 | 264.08 | 31.28 | 0.9882 | 3.89 | 35.752 | 772.2 | 27.612 | -1 | 88.2737 | 9 | 230 | 50 | 229.85 | 145.39 | 31.072 | 0.9298 | 8.37 | 35.713 | 770.4 | 27.52 | -1.2308 | 88.5685 | 9 | 277 | 60 | 276.88 | 131.48 | 31.095 | 0.8541 | 12.042 | 35.601 | 771.2 | 27.459 | -1.1282 | 88.3068 | 9 | 120 | 60 | 119.82 | 179.58 | 21.091 | 0.9802 | 5.044 | 23.804 | 770.7 | 18.35 | -1.1923 | 87.0039 | 9 | 230 | 50 | 229.89 | 105.02 | 21.144 | 0.8758 | 12.239 | 23.808 | 769.4 | 18.321 | -1.359 | 86.6487 | 9 | 277 | 60 | 276.91 | 99.95 | 21.278 | 0.7688 | 17.197 | 23.81 | 770.2 | 18.342 | -1.2564 | 86.2017
| 8 | 120 | 60 | 119.86 | 313.95 | 37.328 | 0.992 | 3.894 | 47.224 | 701.5 | 33.132 | -10.0641 | 88.7591 | 8 | 230 | 50 | 229.81 | 170.57 | 37.172 | 0.9483 | 7.12 | 47.279 | 702.4 | 33.214 | -9.9487 | 89.3522 | 8 | 277 | 60 | 276.86 | 151.4 | 37.263 | 0.889 | 10.038 | 47.27 | 702.8 | 33.229 | -9.8974 | 89.1742 | 8 | 120 | 60 | 119.87 | 238.95 | 28.277 | 0.9872 | 4.045 | 35.533 | 702.7 | 24.975 | -9.9103 | 88.3227 | 8 | 230 | 50 | 229.85 | 133.34 | 28.19 | 0.9198 | 8.578 | 35.485 | 703.1 | 24.952 | -9.859 | 88.5137 | 8 | 277 | 60 | 276.89 | 122.04 | 28.229 | 0.8354 | 13.024 | 35.377 | 703.9 | 24.907 | -9.7564 | 88.232 | 8 | 120 | 60 | 119.83 | 163.58 | 19.139 | 0.9764 | 5.335 | 23.652 | 704.1 | 16.657 | -9.7308 | 87.0317 | 8 | 230 | 50 | 229.9 | 97.16 | 19.211 | 0.86 | 12.806 | 23.656 | 702.9 | 16.631 | -9.8846 | 86.5702 | 8 | 277 | 60 | 276.91 | 93.76 | 19.33 | 0.7445 | 18.429 | 23.657 | 703.5 | 16.645 | -9.8077 | 86.1097
| 7 | 120 | 60 | 119.87 | 260.99 | 30.961 | 0.9897 | 3.683 | 46.747 | 588.1 | 27.498 | -24.6026 | 88.815 | 7 | 230 | 50 | 229.83 | 143.83 | 30.851 | 0.9333 | 7.385 | 46.792 | 588.1 | 27.525 | -24.6026 | 89.2192 | 7 | 277 | 60 | 276.88 | 130.3 | 30.948 | 0.8578 | 11.583 | 46.781 | 588 | 27.511 | -24.6154 | 88.8943 | 7 | 120 | 60 | 119.88 | 198.89 | 23.441 | 0.9832 | 4.023 | 35.168 | 588.7 | 20.705 | -24.5256 | 88.3281 | 7 | 230 | 50 | 229.87 | 113.62 | 23.428 | 0.897 | 9.52 | 35.105 | 589.5 | 20.697 | -24.4231 | 88.343 | 7 | 277 | 60 | 276.9 | 106.7 | 23.475 | 0.7945 | 15.21 | 35.001 | 589.9 | 20.65 | -24.3718 | 87.9659 | 7 | 120 | 60 | 119.84 | 136.56 | 15.857 | 0.9689 | 5.14 | 23.391 | 590.2 | 13.808 | -24.3333 | 87.0783 | 7 | 230 | 50 | 229.91 | 84.25 | 15.954 | 0.8237 | 14.437 | 23.394 | 589.2 | 13.786 | -24.4615 | 86.4109 | 7 | 277 | 60 | 276.92 | 83.6 | 16.064 | 0.6939 | 20.873 | 23.395 | 589.5 | 13.793 | -24.4231 | 85.8628
| 6 | 120 | 60 | 119.88 | 210.74 | 24.904 | 0.9857 | 4.001 | 46.246 | 477.4 | 22.078 | -38.7949 | 88.6524 | 6 | 230 | 50 | 229.84 | 119.01 | 24.855 | 0.9087 | 8.456 | 46.285 | 477.1 | 22.088 | -38.8333 | 88.8674 | 6 | 277 | 60 | 276.89 | 110.95 | 24.976 | 0.8131 | 13.62 | 46.277 | 477.4 | 22.098 | -38.7949 | 88.4769 | 6 | 120 | 60 | 119.89 | 160.87 | 18.831 | 0.9764 | 4.664 | 34.786 | 477.8 | 16.622 | -38.7436 | 88.2693 | 6 | 230 | 50 | 229.88 | 95.23 | 18.871 | 0.8618 | 11.089 | 34.709 | 478.4 | 16.608 | -38.6667 | 88.0081 | 6 | 277 | 60 | 276.91 | 92.47 | 18.921 | 0.7389 | 17.563 | 34.607 | 478.5 | 16.563 | -38.6538 | 87.5377 | 6 | 120 | 60 | 119.86 | 111.25 | 12.736 | 0.9551 | 6.397 | 23.119 | 479.1 | 11.077 | -38.5769 | 86.9739 | 6 | 230 | 50 | 229.92 | 72.43 | 12.867 | 0.7726 | 16.959 | 23.123 | 478.7 | 11.071 | -38.6282 | 86.0418 | 6 | 277 | 60 | 276.93 | 74.11 | 12.958 | 0.6314 | 23.804 | 23.123 | 478.4 | 11.063 | -38.6667 | 85.3758
| 5 | 120 | 60 | 119.89 | 160.13 | 18.773 | 0.9777 | 3.645 | 45.678 | 363.4 | 16.601 | -53.4103 | 88.4302 | 5 | 230 | 50 | 229.86 | 94.78 | 18.847 | 0.8652 | 10.416 | 45.715 | 363.7 | 16.629 | -53.3718 | 88.2315 | 5 | 277 | 60 | 276.87 | 92.25 | 18.977 | 0.743 | 17.618 | 45.711 | 364.4 | 16.657 | -53.2821 | 87.7747 | 5 | 120 | 60 | 119.84 | 123.06 | 14.219 | 0.9642 | 4.682 | 34.349 | 364.3 | 12.515 | -53.2949 | 88.016 | 5 | 230 | 50 | 229.89 | 77.4 | 14.293 | 0.8032 | 13.61 | 34.261 | 364.5 | 12.49 | -53.2692 | 87.3854 | 5 | 277 | 60 | 276.92 | 78.71 | 14.373 | 0.6594 | 21.65 | 34.168 | 364.9 | 12.469 | -53.2179 | 86.7529 | 5 | 120 | 60 | 119.88 | 86.38 | 9.614 | 0.9284 | 7.295 | 22.814 | 365.4 | 8.337 | -53.1538 | 86.7173 | 5 | 230 | 50 | 229.93 | 60.94 | 9.754 | 0.6962 | 20.767 | 22.818 | 365 | 8.328 | -53.2051 | 85.3804 | 5 | 277 | 60 | 276.94 | 64.75 | 9.856 | 0.5496 | 27.738 | 22.819 | 365.3 | 8.337 | -53.1667 | 84.5881
| 4 | 120 | 60 | 119.84 | 112.86 | 12.984 | 0.9599 | 4.993 | 45.048 | 253 | 11.398 | -67.5641 | 87.785 | 4 | 230 | 50 | 229.88 | 72.69 | 13.105 | 0.7841 | 14.695 | 45.08 | 253.2 | 11.415 | -67.5385 | 87.1042 | 4 | 277 | 60 | 276.91 | 75.14 | 13.238 | 0.6364 | 22.654 | 45.08 | 253.99 | 11.451 | -67.4372 | 86.501 | 4 | 120 | 60 | 119.86 | 87.83 | 9.836 | 0.9343 | 6.549 | 33.865 | 253.54 | 8.586 | -67.4949 | 87.2916 | 4 | 230 | 50 | 229.9 | 61.38 | 9.945 | 0.7047 | 18.421 | 33.766 | 253.99 | 8.577 | -67.4372 | 86.2443 | 4 | 277 | 60 | 276.93 | 65.88 | 10.032 | 0.5499 | 26.825 | 33.68 | 254.61 | 8.576 | -67.3577 | 85.4864 | 4 | 120 | 60 | 119.9 | 63.71 | 6.648 | 0.8702 | 10.396 | 22.476 | 254.66 | 5.724 | -67.3513 | 86.1011 | 4 | 230 | 50 | 229.94 | 50.52 | 6.789 | 0.5845 | 26.764 | 22.478 | 254.29 | 5.717 | -67.3987 | 84.2098 | 4 | 277 | 60 | 276.94 | 56.12 | 6.903 | 0.4442 | 32.219 | 22.48 | 254.43 | 5.72 | -67.3808 | 82.8625
| 3 | 120 | 60 | 119.88 | 126.79 | 6.709 | 0.4406 | 92.449 | 44.155 | 123.04 | 5.433 | -84.2256 | 80.9808 | 3 | 230 | 50 | 229.9 | 81.18 | 6.685 | 0.3576 | 56.873 | 44.173 | 122.02 | 5.391 | -84.3564 | 80.6432 | 3 | 277 | 60 | 276.93 | 71.68 | 6.764 | 0.3402 | 41.45 | 44.168 | 122.06 | 5.391 | -84.3513 | 79.7014 | 3 | 120 | 60 | 119.89 | 106.21 | 5.357 | 0.4206 | 92.038 | 33.252 | 130.83 | 4.35 | -83.2269 | 81.2022 | 3 | 230 | 50 | 229.92 | 70.65 | 5.411 | 0.3331 | 48.448 | 33.149 | 131.45 | 4.3575 | -83.1474 | 80.5304 | 3 | 277 | 60 | 276.94 | 60.68 | 5.473 | 0.3257 | 41.246 | 33.061 | 131.35 | 4.3427 | -83.1603 | 79.3477 | 3 | 120 | 60 | 119.91 | 79.5 | 3.774 | 0.3959 | 76.283 | 22.11 | 138.79 | 3.0687 | -82.2064 | 81.3116 | 3 | 230 | 50 | 229.94 | 49.92 | 3.836 | 0.3342 | 42.447 | 22.11 | 138.11 | 3.0537 | -82.2936 | 79.6064 | 3 | 277 | 60 | 276.95 | 48.79 | 3.958 | 0.2929 | 37.425 | 22.114 | 138.77 | 3.0688 | -82.209 | 77.5341
| 2 | 120 | 60 | 119.91 | 37.69 | 1.509 | 0.3342 | 49.291 | 42.779 | 25.887 | 1.1074 | -96.6812 | 73.3863 | 2 | 230 | 50 | 229.91 | 30.7 | 1.629 | 0.2308 | 32.794 | 42.805 | 25.937 | 1.1102 | -96.6747 | 68.1522 | 2 | 277 | 60 | 276.95 | 36.84 | 1.647 | 0.1615 | 28.44 | 42.8 | 25.908 | 1.1089 | -96.6785 | 67.3285 | 2 | 120 | 60 | 119.91 | 31.67 | 1.221 | 0.3214 | 44.399 | 32.179 | 27.607 | 0.8883 | -96.4606 | 72.7518 | 2 | 230 | 50 | 229.93 | 29.124 | 1.326 | 0.198 | 30.694 | 32.073 | 28.184 | 0.9039 | -96.3867 | 68.1674 | 2 | 277 | 60 | 276.95 | 35.69 | 1.352 | 0.1368 | 22.594 | 31.992 | 28.413 | 0.909 | -96.3573 | 67.2337 | 2 | 120 | 60 | 119.93 | 26.282 | 0.9162 | 0.2908 | 43.927 | 21.351 | 30.15 | 0.6438 | -96.1346 | 70.2685 | 2 | 230 | 50 | 229.95 | 27.4 | 0.964 | 0.153 | 25.347 | 21.352 | 29.984 | 0.6402 | -96.1559 | 66.4108 | 2 | 277 | 60 | 276.95 | 34.46 | 0.99 | 0.1038 | 19.516 | 21.353 | 30.089 | 0.6425 | -96.1424 | 64.899
| 1 | 120 | 60 | 119.91 | 21.647 | 0.5503 | 0.212 | 35.37 | 41.963 | 7.218 | 0.3029 | -99.0746 | 55.0427 | 1 | 230 | 50 | 229.91 | 25.768 | 0.566 | 0.0955 | 20.21 | 41.988 | 7.236 | 0.3038 | -99.0723 | 53.6749 | 1 | 277 | 60 | 276.95 | 33.32 | 0.589 | 0.0638 | 16.982 | 41.98 | 7.182 | 0.3015 | -99.0792 | 51.1885 | 1 | 120 | 60 | 119.91 | 20.705 | 0.4418 | 0.1779 | 33.24 | 31.564 | 7.696 | 0.2429 | -99.0133 | 54.9796 | 1 | 230 | 50 | 229.93 | 25.389 | 0.456 | 0.0781 | 18.243 | 31.424 | 7.636 | 0.23993 | -99.021 | 52.6162 | 1 | 277 | 60 | 276.95 | 33.06 | 0.483 | 0.0528 | 11.581 | 31.341 | 7.7 | 0.24132 | -99.0128 | 49.9627 | 1 | 120 | 60 | 119.93 | 25.662 | 0.8723 | 0.2834 | 40.452 | 21.338 | 28.463 | 0.6073 | -96.3509 | 69.6205 | 1 | 230 | 50 | 229.95 | 27.24 | 0.922 | 0.1472 | 26.581 | 21.343 | 28.516 | 0.6086 | -96.3441 | 66.0087 | 1 | 277 | 60 | 276.96 | 34.34 | 0.948 | 0.0996 | 19.519 | 21.343 | 28.58 | 0.61 | -96.3359 | 64.346
| 0 | 120 | 60 | 119.92 | 18.357 | 0.0715 | 0.0325 | 12.127 | 35.209 | 0.0257 | 0.00088 | -99.9967 | 1.2308 | 0 | 230 | 50 | 229.91 | 24.651 | 0.176 | 0.0311 | 11.315 | 35.236 | 0.0255 | 0.00088 | -99.9967 | 0.5 | 0 | 277 | 60 | 276.95 | 32.61 | 0.238 | 0.0264 | 14.439 | 35.235 | 0.0247 | 0.00085 | -99.9968 | 0.35714 | 0 | 120 | 60 | 119.93 | 18.367 | 0.0715 | 0.0325 | 24.535 | 26.239 | 0.0197 | 0.0005 | -99.9975 | 0.6993 | 0 | 230 | 50 | 229.93 | 24.647 | 0.176 | 0.0311 | 11.586 | 26.066 | 0.0195 | 0.00049 | -99.9975 | 0.27841 | 0 | 277 | 60 | 276.96 | 32.59 | 0.237 | 0.0262 | 9.03 | 25.963 | 0.0184 | 0.00048 | -99.9976 | 0.20253 | 0 | 120 | 60 | 119.93 | 18.375 | 0.0717 | 0.0325 | 18.116 | 17.465 | 0.0246 | 0.00043 | -99.9968 | 0.59972 | 0 | 230 | 50 | 229.95 | 24.651 | 0.175 | 0.0308 | 7.349 | 17.507 | 0.0254 | 0.00044 | -99.9967 | 0.25143 | 0 | 277 | 60 | 276.96 | 32.6 | 0.235 | 0.0261 | 7.531 | 17.509 | 0.0255 | 0.00045 | -99.9967 | 0.19149

## Resistor Dimming
Legacy Dimming: Resistor
DER-925 Unit 9
| 48V LED, 120 VAC | [12 empty] | 48V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 36V LED, 120 VAC | [12 empty] | 36V LED, 230 VAC | [12 empty] | 36V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
|  | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
|  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 100 | 120 | 60 | 119.88 | 349.33 | 41.482 | 0.9906 | 4.431 | 47.792 | 770.3 | 36.821 | -1.2436 | 88.7638 | 100 | 230 | 50 | 229.9 | 187.57 | 41.04 | 0.9517 | 6.887 | 47.704 | 770 | 36.738 | -1.2821 | 89.5175 | 100 | 277 | 60 | 276.93 | 165.41 | 41.235 | 0.9001 | 9.147 | 47.787 | 771 | 36.848 | -1.1538 | 89.361 | 100 | 120 | 60 | 119.9 | 266.76 | 31.52 | 0.9853 | 3.785 | 36.138 | 770.5 | 27.848 | -1.2179 | 88.3503 | 100 | 230 | 50 | 229.93 | 148.39 | 31.592 | 0.9258 | 8.421 | 36.3 | 771.3 | 28.005 | -1.1154 | 88.6459 | 100 | 277 | 50 | 276.92 | 129.96 | 31.536 | 0.8763 | 11.379 | 36.222 | 770 | 27.897 | -1.2821 | 88.4608 | 100 | 120 | 60 | 119.92 | 180.77 | 21.111 | 0.9738 | 5.358 | 23.83 | 770.3 | 18.359 | -1.2436 | 86.9641 | 100 | 230 | 50 | 229.94 | 106.2 | 21.13 | 0.8654 | 12.106 | 23.822 | 769.2 | 18.327 | -1.3846 | 86.7345 | 100 | 277 | 60 | 276.95 | 100.94 | 21.233 | 0.7596 | 17.549 | 23.814 | 769.7 | 18.333 | -1.3205 | 86.342
| 90 | 120 | 60 | 119.88 | 349.21 | 41.466 | 0.9906 | 4.28 | 47.778 | 770.2 | 36.806 | -1.2564 | 88.7619 | 90 | 230 | 50 | 229.9 | 187.49 | 41.017 | 0.9517 | 7.042 | 47.692 | 769.8 | 36.72 | -1.3077 | 89.5239 | 90 | 277 | 60 | 276.93 | 165.35 | 41.206 | 0.8999 | 9.21 | 47.773 | 770.8 | 36.834 | -1.1795 | 89.3899 | 90 | 120 | 60 | 119.91 | 266.64 | 31.5 | 0.9853 | 3.764 | 36.131 | 770.3 | 27.839 | -1.2436 | 88.3778 | 90 | 230 | 50 | 229.93 | 148.28 | 31.563 | 0.9258 | 8.486 | 36.288 | 771.1 | 27.986 | -1.141 | 88.6671 | 90 | 277 | 50 | 276.92 | 129.88 | 31.515 | 0.8762 | 11.328 | 36.212 | 769.8 | 27.882 | -1.3077 | 88.4722 | 90 | 120 | 60 | 119.92 | 180.71 | 21.102 | 0.9738 | 4.927 | 23.826 | 770.2 | 18.354 | -1.2564 | 86.9775 | 90 | 230 | 50 | 229.94 | 106.17 | 21.123 | 0.8653 | 12.193 | 23.819 | 769.1 | 18.322 | -1.3974 | 86.7396 | 90 | 277 | 60 | 276.95 | 100.92 | 21.227 | 0.7595 | 16.949 | 23.811 | 769.6 | 18.328 | -1.3333 | 86.3429
| 80 | 120 | 60 | 119.88 | 341.62 | 40.56 | 0.9904 | 4.466 | 47.686 | 754.8 | 36.002 | -3.2308 | 88.7623 | 80 | 230 | 50 | 229.9 | 183.74 | 40.143 | 0.9503 | 7.015 | 47.604 | 754.7 | 35.933 | -3.2436 | 89.5125 | 80 | 277 | 60 | 276.94 | 162.2 | 40.293 | 0.8969 | 9.826 | 47.679 | 754.9 | 36 | -3.2179 | 89.3455 | 80 | 120 | 60 | 119.91 | 260.76 | 30.79 | 0.9848 | 4.135 | 36.06 | 754.6 | 27.215 | -3.2564 | 88.3891 | 80 | 230 | 50 | 229.94 | 145.16 | 30.819 | 0.9234 | 8.217 | 36.21 | 754.5 | 27.326 | -3.2692 | 88.6661 | 80 | 277 | 50 | 276.92 | 127.5 | 30.809 | 0.8726 | 10.957 | 36.139 | 753.9 | 27.252 | -3.3462 | 88.4547 | 80 | 120 | 60 | 119.92 | 176.77 | 20.621 | 0.9728 | 4.877 | 23.785 | 754.1 | 17.939 | -3.3205 | 86.9938 | 80 | 230 | 50 | 229.94 | 104.21 | 20.635 | 0.8612 | 12.288 | 23.777 | 752.7 | 17.9 | -3.5 | 86.7458 | 80 | 277 | 60 | 276.95 | 99.38 | 20.74 | 0.7536 | 17.554 | 23.77 | 753.1 | 17.906 | -3.4487 | 86.3356
| 70 | 120 | 60 | 119.89 | 283.58 | 33.571 | 0.9874 | 3.9 | 47.03 | 634 | 29.821 | -18.7179 | 88.8296 | 70 | 230 | 50 | 229.9 | 154.88 | 33.286 | 0.9348 | 7.245 | 46.951 | 633.5 | 29.748 | -18.7821 | 89.3709 | 70 | 277 | 60 | 276.94 | 139.17 | 33.413 | 0.8671 | 11.061 | 47.02 | 633.5 | 29.788 | -18.7821 | 89.1509 | 70 | 120 | 60 | 119.91 | 216.9 | 25.49 | 0.9802 | 4.472 | 35.546 | 634.1 | 22.544 | -18.7051 | 88.4425 | 70 | 230 | 50 | 229.94 | 123.51 | 25.584 | 0.9009 | 8.905 | 35.688 | 634.4 | 22.645 | -18.6667 | 88.5124 | 70 | 277 | 50 | 276.92 | 110.15 | 25.59 | 0.8389 | 12.314 | 35.621 | 633.8 | 22.58 | -18.7436 | 88.2376 | 70 | 120 | 60 | 119.92 | 148.12 | 17.102 | 0.9628 | 6.008 | 23.493 | 633.5 | 14.886 | -18.7821 | 87.0425 | 70 | 230 | 50 | 229.94 | 90.49 | 17.171 | 0.8252 | 14.112 | 23.485 | 632.8 | 14.864 | -18.8718 | 86.5646 | 70 | 277 | 60 | 276.95 | 88.61 | 17.261 | 0.7033 | 20.559 | 23.479 | 633 | 14.865 | -18.8462 | 86.119
| 60 | 120 | 60 | 119.89 | 226.91 | 26.738 | 0.9827 | 3.262 | 46.324 | 512.6 | 23.747 | -34.2821 | 88.8137 | 60 | 230 | 50 | 229.91 | 127.16 | 26.623 | 0.9106 | 8.328 | 46.252 | 512.5 | 23.708 | -34.2949 | 89.0508 | 60 | 277 | 60 | 276.94 | 117.58 | 26.783 | 0.8225 | 12.882 | 46.321 | 513.4 | 23.786 | -34.1795 | 88.8101 | 60 | 120 | 60 | 119.91 | 174.5 | 20.34 | 0.9718 | 4.117 | 34.993 | 513.3 | 17.964 | -34.1923 | 88.3186 | 60 | 230 | 50 | 229.94 | 102.87 | 20.464 | 0.8652 | 10.233 | 35.129 | 513.9 | 18.055 | -34.1154 | 88.2281 | 60 | 277 | 50 | 276.93 | 93.76 | 20.501 | 0.7895 | 14.412 | 35.067 | 513.5 | 18.009 | -34.1667 | 87.8445 | 60 | 120 | 60 | 119.93 | 120.6 | 13.689 | 0.9464 | 6.299 | 23.185 | 513.4 | 11.906 | -34.1795 | 86.9749 | 60 | 230 | 50 | 229.95 | 77.62 | 13.782 | 0.7721 | 15.968 | 23.178 | 512.9 | 11.89 | -34.2436 | 86.2719 | 60 | 277 | 60 | 276.95 | 78.35 | 13.864 | 0.6389 | 23.352 | 23.171 | 513 | 11.889 | -34.2308 | 85.7545
| 50 | 120 | 60 | 119.9 | 173.15 | 20.205 | 0.9733 | 4.724 | 45.569 | 392.6 | 17.892 | -49.6667 | 88.5523 | 50 | 230 | 50 | 229.91 | 101.05 | 20.122 | 0.8662 | 10.513 | 45.495 | 391.5 | 17.814 | -49.8077 | 88.53 | 50 | 277 | 60 | 276.94 | 97.23 | 20.262 | 0.7525 | 16.15 | 45.558 | 392 | 17.863 | -49.7436 | 88.1601 | 50 | 120 | 60 | 119.92 | 133.14 | 15.272 | 0.9566 | 5.088 | 34.387 | 391.2 | 13.455 | -49.8462 | 88.1024 | 50 | 230 | 50 | 229.94 | 83.36 | 15.437 | 0.8055 | 13.613 | 34.515 | 392 | 13.532 | -49.7436 | 87.6595 | 50 | 277 | 50 | 276.93 | 78.31 | 15.483 | 0.714 | 17.847 | 34.459 | 391.8 | 13.501 | -49.7692 | 87.1989 | 50 | 120 | 60 | 119.93 | 94.2 | 10.323 | 0.9137 | 6.683 | 22.848 | 391.8 | 8.954 | -49.7692 | 86.7384 | 50 | 230 | 50 | 229.95 | 65.48 | 10.432 | 0.6929 | 19.579 | 22.842 | 391.4 | 8.943 | -49.8205 | 85.7266 | 50 | 277 | 60 | 276.95 | 68.44 | 10.515 | 0.5547 | 26.556 | 22.837 | 391.6 | 8.945 | -49.7949 | 85.0689
| 40 | 120 | 60 | 119.9 | 121.74 | 13.858 | 0.9496 | 4.369 | 44.723 | 272.2 | 12.175 | -65.1026 | 87.8554 | 40 | 230 | 50 | 229.92 | 77.07 | 13.845 | 0.7812 | 13.545 | 44.653 | 271.25 | 12.113 | -65.2244 | 87.4901 | 40 | 277 | 60 | 276.95 | 78.74 | 13.987 | 0.6415 | 22.17 | 44.716 | 272.03 | 12.165 | -65.1244 | 86.9736 | 40 | 120 | 60 | 119.92 | 94.95 | 10.456 | 0.918 | 5.641 | 33.723 | 271.2 | 9.146 | -65.2308 | 87.4713 | 40 | 230 | 50 | 229.95 | 65.81 | 10.609 | 0.7011 | 18.095 | 33.84 | 271.54 | 9.19 | -65.1872 | 86.6246 | 40 | 277 | 50 | 276.93 | 64.33 | 10.672 | 0.5991 | 23.977 | 33.789 | 271.5 | 9.175 | -65.1923 | 85.9726 | 40 | 120 | 60 | 119.93 | 70.01 | 7.08 | 0.8432 | 11.721 | 22.475 | 271.49 | 6.102 | -65.1936 | 86.1864 | 40 | 230 | 50 | 229.95 | 54.54 | 7.2 | 0.5741 | 26.632 | 22.469 | 271.22 | 6.095 | -65.2282 | 84.6528 | 40 | 277 | 60 | 276.96 | 59.29 | 7.298 | 0.4445 | 32.823 | 22.465 | 271.57 | 6.101 | -65.1833 | 83.5982
| 30 | 120 | 60 | 119.91 | 140.13 | 7.043 | 0.4183 | 98.364 | 43.59 | 131.29 | 5.723 | -83.1679 | 81.258 | 30 | 230 | 50 | 229.92 | 86.14 | 7.033 | 0.3549 | 57.077 | 43.533 | 131.29 | 5.716 | -83.1679 | 81.274 | 30 | 277 | 60 | 276.95 | 77.76 | 7.121 | 0.3303 | 42.594 | 43.587 | 131.73 | 5.742 | -83.1115 | 80.6347 | 30 | 120 | 60 | 119.93 | 114.51 | 5.661 | 0.4128 | 89.5 | 32.924 | 140.35 | 4.6212 | -82.0064 | 81.6322 | 30 | 230 | 50 | 229.95 | 75.33 | 5.696 | 0.3285 | 51.633 | 33.025 | 139.95 | 4.6215 | -82.0577 | 81.1359 | 30 | 277 | 50 | 276.93 | 64.4 | 5.744 | 0.3226 | 42.234 | 32.98 | 140.06 | 4.62 | -82.0436 | 80.4318 | 30 | 120 | 60 | 119.93 | 87 | 4.001 | 0.3838 | 78.243 | 22.083 | 147.84 | 3.2647 | -81.0462 | 81.5971 | 30 | 230 | 50 | 229.95 | 56.06 | 4.029 | 0.3126 | 43.395 | 22.075 | 146.92 | 3.2432 | -81.1641 | 80.4964 | 30 | 277 | 60 | 276.96 | 52.45 | 4.128 | 0.2841 | 40.442 | 22.071 | 147.17 | 3.2479 | -81.1321 | 78.6797
| 20 | 120 | 60 | 119.92 | 42.35 | 1.466 | 0.289 | 46.811 | 42.014 | 25.733 | 1.0812 | -96.7009 | 73.7517 | 20 | 230 | 50 | 229.92 | 34.41 | 1.555 | 0.1965 | 35.92 | 41.956 | 25.71 | 1.0787 | -96.7038 | 69.3698 | 20 | 277 | 60 | 276.95 | 39.53 | 1.57 | 0.1434 | 25.677 | 42.006 | 25.81 | 1.0842 | -96.691 | 69.0573 | 20 | 120 | 60 | 119.93 | 37.28 | 1.183 | 0.2645 | 45.627 | 31.639 | 27.348 | 0.8652 | -96.4938 | 73.1361 | 20 | 230 | 50 | 229.95 | 33.13 | 1.233 | 0.1619 | 29.955 | 31.731 | 26.911 | 0.8539 | -96.5499 | 69.2539 | 20 | 277 | 50 | 276.93 | 34.72 | 1.25 | 0.13 | 27.791 | 31.692 | 27.156 | 0.8606 | -96.5185 | 68.848 | 20 | 120 | 60 | 119.94 | 33.18 | 0.88 | 0.2213 | 41.274 | 21.257 | 29.255 | 0.6219 | -96.2494 | 70.6705 | 20 | 230 | 50 | 229.95 | 31.85 | 0.916 | 0.1251 | 25.24 | 21.255 | 29.362 | 0.6241 | -96.2356 | 68.1332 | 20 | 277 | 60 | 276.95 | 37.48 | 0.931 | 0.0897 | 19.148 | 21.251 | 29.465 | 0.6262 | -96.2224 | 67.261
| 10 | 120 | 60 | 119.92 | 29.569 | 0.5453 | 0.1538 | 43.807 | 41.227 | 7.38 | 0.3043 | -99.0538 | 55.8041 | 10 | 230 | 50 | 229.92 | 30.29 | 0.52 | 0.0747 | 24.118 | 41.143 | 7.077 | 0.2912 | -99.0927 | 56 | 10 | 277 | 60 | 276.95 | 36.42 | 0.542 | 0.0537 | 20.185 | 41.204 | 7.218 | 0.2974 | -99.0746 | 54.8708 | 10 | 120 | 60 | 119.93 | 29.073 | 0.427 | 0.1224 | 32.877 | 31.013 | 7.709 | 0.23908 | -99.0117 | 55.9906 | 10 | 230 | 50 | 229.95 | 30.19 | 0.426 | 0.0614 | 22.547 | 31.118 | 7.651 | 0.2381 | -99.0191 | 55.892 | 10 | 277 | 50 | 276.93 | 32.38 | 0.438 | 0.0489 | 20.359 | 31.072 | 7.661 | 0.23806 | -99.0178 | 54.3516 | 10 | 120 | 60 | 119.94 | 33.06 | 0.882 | 0.2226 | 41.592 | 21.262 | 29.206 | 0.621 | -96.2556 | 70.4082 | 10 | 230 | 50 | 229.95 | 31.84 | 0.914 | 0.1248 | 29.623 | 21.261 | 29.317 | 0.6233 | -96.2414 | 68.1947 | 10 | 277 | 60 | 276.96 | 37.47 | 0.927 | 0.0894 | 19.676 | 21.256 | 29.406 | 0.6251 | -96.23 | 67.4326
| 0 | 120 | 60 | 119.92 | 27.288 | 0.0648 | 0.0198 | 13.015 | 35.394 | 0.0082 | 0.00028 | -99.9989 | 0.4321 | 0 | 230 | 50 | 229.92 | 29.427 | 0.152 | 0.0224 | 6.72 | 35.3 | 0.0073 | 0.00025 | -99.9991 | 0.16447 | 0 | 277 | 60 | 276.95 | 35.79 | 0.2 | 0.0202 | 17.364 | 35.386 | 0.0061 | 0.00021 | -99.9992 | 0.105 | 0 | 120 | 60 | 119.93 | 27.514 | 0.066 | 0.0199 | 12.923 | 26.367 | 0.0045 | 0.00011 | -99.9994 | 0.16667 | 0 | 230 | 50 | 229.95 | 29.594 | 0.151 | 0.0222 | 6.973 | 26.535 | 0.0041 | 0.0001 | -99.9995 | 0.066225 | 0 | 277 | 50 | 276.93 | 31.94 | 0.198 | 0.0224 | 6.631 | 26.459 | 0.0036 | 9e-05 | -99.9995 | 0.045455 | 0 | 120 | 60 | 119.94 | 27.589 | 0.065 | 0.0195 | 35.098 | 17.544 | 0.0029 | 5e-05 | -99.9996 | 0.076923 | 0 | 230 | 50 | 229.95 | 29.599 | 0.151 | 0.0221 | 6.484 | 17.551 | 0.0034 | 6e-05 | -99.9996 | 0.039735 | 0 | 277 | 60 | 276.96 | 35.83 | 0.201 | 0.0202 | 7.76 | 17.548 | 0.0033 | 6e-05 | -99.9996 | 0.029851

## PWM Dimming 400 Hz
Legacy Dimming: PWM (400 Hz)
DER-925 Unit 9
| 48V LED, 120 VAC | [12 empty] | 48V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 36V LED, 120 VAC | [12 empty] | 36V LED, 230 VAC | [12 empty] | 36V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
|  | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
|  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 100 | [12 empty] | 100 | 230 | 50 | 229.82 | 188.77 | 41.374 | 0.9536 | 6.876 | 47.841 | 773 | 36.946 | -0.89744 | 89.2976 | 100 | [12 empty] | 100 | [12 empty] | 100 | [12 empty] | 100 | [12 empty] | 100 | [12 empty] | 100 | [12 empty] | 100
| 90 | [12 empty] | 90 | 230 | 50 | 229.82 | 188.62 | 41.336 | 0.9536 | 7.174 | 47.823 | 772.6 | 36.916 | -0.94872 | 89.3071 | 90 | [12 empty] | 90 | [12 empty] | 90 | [12 empty] | 90 | [12 empty] | 90 | [12 empty] | 90 | [12 empty] | 90
| 80 | [12 empty] | 80 | 230 | 50 | 229.83 | 164 | 35.523 | 0.9424 | 7.043 | 47.272 | 671 | 31.69 | -13.9744 | 89.2098 | 80 | [12 empty] | 80 | [12 empty] | 80 | [12 empty] | 80 | [12 empty] | 80 | [12 empty] | 80 | [12 empty] | 80
| 70 | [12 empty] | 70 | 230 | 50 | 229.85 | 138.26 | 29.376 | 0.9245 | 7.905 | 46.648 | 561 | 26.139 | -28.0769 | 88.9808 | 70 | [12 empty] | 70 | [12 empty] | 70 | [12 empty] | 70 | [12 empty] | 70 | [12 empty] | 70 | [12 empty] | 70
| 60 | [12 empty] | 60 | 230 | 50 | 229.87 | 113.79 | 23.412 | 0.895 | 9.089 | 45.981 | 451.4 | 20.734 | -42.1282 | 88.5614 | 60 | [12 empty] | 60 | [12 empty] | 60 | [12 empty] | 60 | [12 empty] | 60 | [12 empty] | 60 | [12 empty] | 60
| 50 | [12 empty] | 50 | 230 | 50 | 229.88 | 90.62 | 17.585 | 0.8441 | 10.936 | 45.256 | 341.7 | 15.446 | -56.1923 | 87.8362 | 50 | [12 empty] | 50 | [12 empty] | 50 | [12 empty] | 50 | [12 empty] | 50 | [12 empty] | 50 | [12 empty] | 50
| 40 | [12 empty] | 40 | 230 | 50 | 229.9 | 69.45 | 11.924 | 0.7467 | 15.506 | 44.446 | 232.56 | 10.326 | -70.1846 | 86.5985 | 40 | [12 empty] | 40 | [12 empty] | 40 | [12 empty] | 40 | [12 empty] | 40 | [12 empty] | 40 | [12 empty] | 40
| 30 | [12 empty] | 30 | 230 | 50 | 229.91 | 74.57 | 5.833 | 0.3406 | 50.804 | 43.362 | 107.97 | 4.681 | -86.1577 | 80.2503 | 30 | [12 empty] | 30 | [12 empty] | 30 | [12 empty] | 30 | [12 empty] | 30 | [12 empty] | 30 | [12 empty] | 30
| 20 | [12 empty] | 20 | 230 | 50 | 229.93 | 29.388 | 0.732 | 0.1083 | 28.082 | 41.435 | 10.086 | 0.4179 | -98.7069 | 57.0902 | 20 | [12 empty] | 20 | [12 empty] | 20 | [12 empty] | 20 | [12 empty] | 20 | [12 empty] | 20 | [12 empty] | 20
| 10 | [12 empty] | 10 | 230 | 50 | 229.93 | 28.816 | 0.557 | 0.084 | 26.009 | 41.246 | 7.224 | 0.2979 | -99.0738 | 53.4829 | 10 | [12 empty] | 10 | [12 empty] | 10 | [12 empty] | 10 | [12 empty] | 10 | [12 empty] | 10 | [12 empty] | 10
| 0 | [12 empty] | 0 | 230 | 50 | 229.93 | 27.874 | 0.18 | 0.0281 | 19.818 | 35.917 | 0 | 0.00034 | -100 | 0.18889 | 0 | [12 empty] | 0 | [12 empty] | 0 | [12 empty] | 0 | [12 empty] | 0 | [12 empty] | 0 | [12 empty] | 0
s

## PWM Dimming 2000 Hz
Legacy Dimming: PWM (2000 Hz)
DER-925 Unit 9
| 48V LED, 120 VAC | [12 empty] | 48V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 36V LED, 120 VAC | [12 empty] | 36V LED, 230 VAC | [12 empty] | 36V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
|  | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
|  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
| 100 | 120 | 60 | 119.9 | 348.83 | 41.481 | 0.9917 | 4.143 | 47.701 | 771.1 | 36.747 | -1.141 | 88.5875 | 100 | 230 | 50 | 229.95 | 187.35 | 41.06 | 0.9531 | 6.777 | 47.646 | 770.7 | 36.689 | -1.1923 | 89.3546 | 100 | 277 | 60 | 276.97 | 164.59 | 41.07 | 0.9011 | 9.054 | 47.596 | 770.6 | 36.641 | -1.2051 | 89.216 | 100 | 120 | 60 | 119.91 | 265.22 | 31.386 | 0.9869 | 4.315 | 36.012 | 769.9 | 27.699 | -1.2949 | 88.2527 | 100 | 239 | 50 | 238.89 | 142.16 | 31.222 | 0.9193 | 8.837 | 36.004 | 768.5 | 27.64 | -1.4744 | 88.5273 | 100 | 277 | 60 | 276.91 | 132.78 | 31.402 | 0.854 | 12.492 | 36.021 | 770.4 | 27.725 | -1.2308 | 88.2906 | 100 | 120 | 60 | 119.84 | 179.8 | 21.035 | 0.9763 | 5.915 | 23.752 | 770 | 18.27 | -1.2821 | 86.8552 | 100 | 230 | 50 | 229.92 | 105.54 | 21.103 | 0.8697 | 12.18 | 23.764 | 768.9 | 18.253 | -1.4231 | 86.4948 | 100 | 277 | 60 | 276.94 | 100.32 | 21.218 | 0.7637 | 17.939 | 23.74 | 769.8 | 18.255 | -1.3077 | 86.0354
| 90 | 120 | 60 | 119.91 | 307.56 | 36.531 | 0.9906 | 3.627 | 47.242 | 686.3 | 32.394 | -12.0128 | 88.6754 | 90 | 230 | 50 | 229.95 | 167.06 | 36.27 | 0.9441 | 7.335 | 47.195 | 686.7 | 32.377 | -11.9615 | 89.2666 | 90 | 277 | 60 | 276.9 | 148.21 | 36.266 | 0.8837 | 9.901 | 47.142 | 685.9 | 32.306 | -12.0641 | 89.0807 | 90 | 120 | 60 | 119.92 | 234.75 | 27.725 | 0.9849 | 4.536 | 35.665 | 687.4 | 24.49 | -11.8718 | 88.3318 | 90 | 239 | 50 | 238.9 | 128.07 | 27.677 | 0.9047 | 9.069 | 35.661 | 686.8 | 24.468 | -11.9487 | 88.4055 | 90 | 277 | 60 | 276.92 | 121.01 | 27.805 | 0.8298 | 12.889 | 35.673 | 687.8 | 24.513 | -11.8205 | 88.1604 | 90 | 120 | 60 | 119.85 | 159.77 | 18.583 | 0.9705 | 5.302 | 23.55 | 686.3 | 16.148 | -12.0128 | 86.8966 | 90 | 230 | 50 | 229.92 | 95.77 | 18.682 | 0.8485 | 13.42 | 23.563 | 685.8 | 16.141 | -12.0769 | 86.3987 | 90 | 277 | 60 | 276.94 | 92.71 | 18.799 | 0.7322 | 18.473 | 23.541 | 686.2 | 16.136 | -12.0256 | 85.8344
| 80 | 120 | 60 | 119.91 | 261.46 | 30.981 | 0.9882 | 3.493 | 46.691 | 588.5 | 27.448 | -24.5513 | 88.5962 | 80 | 230 | 50 | 229.89 | 143.92 | 30.79 | 0.9304 | 7.283 | 46.65 | 589.3 | 27.471 | -24.4487 | 89.2205 | 80 | 277 | 60 | 276.91 | 130.09 | 30.794 | 0.855 | 12.355 | 46.597 | 587.9 | 27.363 | -24.6282 | 88.8582 | 80 | 120 | 60 | 119.92 | 198.35 | 23.31 | 0.98 | 4.016 | 35.214 | 585.1 | 20.584 | -24.9872 | 88.3054 | 80 | 239 | 50 | 238.91 | 111.08 | 23.349 | 0.8799 | 10.62 | 35.214 | 585.3 | 20.589 | -24.9615 | 88.1794 | 80 | 277 | 60 | 276.93 | 107.12 | 23.477 | 0.7914 | 14.798 | 35.227 | 586.4 | 20.636 | -24.8205 | 87.8988 | 80 | 120 | 60 | 119.87 | 136.52 | 15.737 | 0.9616 | 5.143 | 23.305 | 587.5 | 13.676 | -24.6795 | 86.9035 | 80 | 230 | 50 | 229.93 | 84.66 | 15.855 | 0.8145 | 14.387 | 23.316 | 587 | 13.669 | -24.7436 | 86.2126 | 80 | 277 | 60 | 276.95 | 83.91 | 15.946 | 0.6861 | 20.682 | 23.297 | 587.1 | 13.661 | -24.7308 | 85.6704
| 70 | 120 | 60 | 119.92 | 214.46 | 25.283 | 0.9833 | 4.137 | 46.091 | 486.6 | 22.409 | -37.6154 | 88.6327 | 70 | 230 | 50 | 229.9 | 120.89 | 25.205 | 0.9068 | 8.896 | 46.041 | 486.3 | 22.366 | -37.6538 | 88.7364 | 70 | 277 | 60 | 276.93 | 112.25 | 25.274 | 0.8129 | 14.042 | 46 | 486.6 | 22.363 | -37.6154 | 88.4822 | 70 | 120 | 60 | 119.93 | 164.72 | 19.206 | 0.9724 | 4.103 | 34.762 | 487.9 | 16.944 | -37.4487 | 88.2224 | 70 | 239 | 50 | 238.92 | 95.53 | 19.285 | 0.845 | 11.468 | 34.76 | 487.8 | 16.936 | -37.4615 | 87.8195 | 70 | 277 | 60 | 276.94 | 94.38 | 19.37 | 0.741 | 18.118 | 34.767 | 487.7 | 16.938 | -37.4744 | 87.4445 | 70 | 120 | 60 | 119.88 | 114.29 | 12.981 | 0.9473 | 6.736 | 23.049 | 489.8 | 11.278 | -37.2051 | 86.8808 | 70 | 230 | 50 | 229.94 | 74.33 | 13.131 | 0.7682 | 17.038 | 23.063 | 489.8 | 11.284 | -37.2051 | 85.934 | 70 | 277 | 60 | 276.96 | 75.67 | 13.215 | 0.6306 | 24.85 | 23.043 | 489.5 | 11.267 | -37.2436 | 85.2592
| 60 | 120 | 60 | 119.93 | 174.63 | 20.452 | 0.9762 | 5.099 | 45.527 | 397.5 | 18.076 | -49.0385 | 88.3826 | 60 | 230 | 50 | 229.92 | 101.56 | 20.398 | 0.8734 | 9.654 | 45.477 | 396.8 | 18.023 | -49.1282 | 88.3567 | 60 | 277 | 60 | 276.94 | 97.31 | 20.475 | 0.7598 | 15.741 | 45.434 | 396.9 | 18.009 | -49.1154 | 87.956 | 60 | 120 | 60 | 119.87 | 133.67 | 15.402 | 0.9612 | 5.719 | 34.305 | 395.7 | 13.561 | -49.2692 | 88.047 | 60 | 239 | 50 | 238.93 | 81.59 | 15.531 | 0.7968 | 13.541 | 34.303 | 395.6 | 13.556 | -49.2821 | 87.2835 | 60 | 277 | 60 | 276.95 | 83.15 | 15.636 | 0.6791 | 21.273 | 34.317 | 396.5 | 13.591 | -49.1667 | 86.9212 | 60 | 120 | 60 | 119.9 | 93.91 | 10.394 | 0.9231 | 8.022 | 22.787 | 395.6 | 9.001 | -49.2821 | 86.598 | 60 | 230 | 50 | 229.95 | 64.8 | 10.525 | 0.706 | 19.23 | 22.797 | 394.4 | 8.967 | -49.4359 | 85.1971 | 60 | 277 | 60 | 276.96 | 68.02 | 10.642 | 0.5649 | 27.774 | 22.787 | 396.6 | 9.015 | -49.1538 | 84.7115
| 50 | 120 | 60 | 119.87 | 129.79 | 14.948 | 0.9601 | 4.07 | 44.812 | 293.75 | 13.145 | -62.3397 | 87.9382 | 50 | 230 | 50 | 229.93 | 80.95 | 15.088 | 0.8104 | 12.5 | 44.777 | 294.91 | 13.184 | -62.191 | 87.3807 | 50 | 277 | 60 | 276.95 | 81.29 | 15.125 | 0.6716 | 20.125 | 44.729 | 293.66 | 13.126 | -62.3513 | 86.7835 | 50 | 120 | 60 | 119.89 | 101.02 | 11.335 | 0.936 | 5.272 | 33.759 | 294.32 | 9.933 | -62.2667 | 87.6312 | 50 | 239 | 50 | 238.94 | 67.34 | 11.491 | 0.7143 | 18.32 | 33.755 | 293.79 | 9.901 | -62.3346 | 86.1631 | 50 | 277 | 60 | 276.96 | 71.27 | 11.58 | 0.5869 | 24.546 | 33.765 | 294.27 | 9.925 | -62.2731 | 85.7081 | 50 | 120 | 60 | 119.91 | 73.43 | 7.703 | 0.8746 | 11.133 | 22.486 | 295.96 | 6.644 | -62.0564 | 86.2521 | 50 | 230 | 50 | 229.95 | 55.58 | 7.866 | 0.6153 | 24.877 | 22.497 | 295.8 | 6.645 | -62.0769 | 84.4775 | 50 | 277 | 60 | 276.97 | 60.2 | 7.949 | 0.4768 | 30.665 | 22.482 | 295.41 | 6.635 | -62.1269 | 83.4696
| 40 | 120 | 60 | 119.9 | 88.04 | 9.683 | 0.9172 | 7.511 | 44.01 | 191.37 | 8.412 | -75.4654 | 86.8739 | 40 | 230 | 50 | 229.95 | 61.73 | 9.786 | 0.6893 | 18.227 | 43.965 | 190.78 | 8.387 | -75.541 | 85.7041 | 40 | 277 | 60 | 276.96 | 66.9 | 10.161 | 0.5483 | 25.883 | 43.977 | 196.38 | 8.623 | -74.8231 | 84.8637 | 40 | 120 | 60 | 119.91 | 69.98 | 7.293 | 0.869 | 7.881 | 33.124 | 190.67 | 6.307 | -75.5551 | 86.4802 | 40 | 239 | 50 | 238.95 | 53.95 | 7.465 | 0.579 | 23.831 | 33.126 | 191.25 | 6.329 | -75.4808 | 84.7823 | 40 | 277 | 60 | 276.97 | 59.77 | 7.622 | 0.4608 | 30.117 | 33.136 | 191.78 | 6.348 | -75.4128 | 83.2852 | 40 | 120 | 60 | 119.92 | 54.3 | 4.984 | 0.7655 | 13.92 | 22.121 | 191.91 | 4.241 | -75.3962 | 85.0923 | 40 | 230 | 50 | 229.96 | 46.82 | 5.149 | 0.4781 | 31.012 | 22.134 | 192.23 | 4.253 | -75.3551 | 82.5986 | 40 | 277 | 60 | 276.98 | 53.43 | 5.262 | 0.3555 | 34.871 | 22.123 | 192.39 | 4.251 | -75.3346 | 80.7868
| 30 | 120 | 60 | 119.92 | 92.84 | 4.718 | 0.4235 | 79.813 | 43.032 | 88.55 | 3.807 | -88.6474 | 80.691 | 30 | 230 | 50 | 229.96 | 61.9 | 4.759 | 0.3346 | 43.803 | 42.989 | 88.28 | 3.796 | -88.6821 | 79.7647 | 30 | 277 | 60 | 276.97 | 56.46 | 4.896 | 0.3132 | 40.941 | 42.961 | 88.68 | 3.801 | -88.6308 | 77.6348 | 30 | 120 | 60 | 119.93 | 80.57 | 3.783 | 0.3918 | 77.654 | 32.428 | 94.22 | 3.052 | -87.9205 | 80.6767 | 30 | 239 | 50 | 238.96 | 50.27 | 3.873 | 0.3225 | 40.797 | 32.428 | 94.22 | 3.054 | -87.9205 | 78.8536 | 30 | 277 | 60 | 276.97 | 50.22 | 3.985 | 0.2864 | 37.377 | 32.436 | 94.4 | 3.057 | -87.8974 | 76.7127 | 30 | 120 | 60 | 119.94 | 61.89 | 2.679 | 0.3618 | 63.575 | 21.748 | 97.84 | 2.1283 | -87.4564 | 79.4438 | 30 | 230 | 50 | 229.97 | 41.22 | 2.784 | 0.2936 | 41.21 | 21.767 | 99 | 2.152 | -87.3077 | 77.2989 | 30 | 277 | 60 | 276.98 | 44.05 | 2.912 | 0.2386 | 35.149 | 21.759 | 99.13 | 2.156 | -87.291 | 74.0385
| 20 | 120 | 60 | 119.94 | 26.956 | 0.5275 | 0.1631 | 46.693 | 41.115 | 7.057 | 0.2901 | -99.0953 | 54.9953 | 20 | 230 | 50 | 229.97 | 28.529 | 0.556 | 0.0847 | 25.404 | 41.092 | 7.283 | 0.2993 | -99.0663 | 53.8309 | 20 | 277 | 60 | 276.98 | 35.1 | 0.569 | 0.0585 | 21.478 | 41.042 | 7.113 | 0.2919 | -99.0881 | 51.3005 | 20 | 120 | 60 | 119.95 | 26.242 | 0.4318 | 0.1372 | 32.539 | 30.911 | 7.749 | 0.2395 | -99.0065 | 55.4655 | 20 | 239 | 50 | 238.97 | 28.691 | 0.453 | 0.0661 | 15.33 | 30.905 | 7.646 | 0.2363 | -99.0197 | 52.1634 | 20 | 277 | 60 | 276.98 | 34.9 | 0.477 | 0.0494 | 11.713 | 30.913 | 7.661 | 0.2368 | -99.0178 | 49.6436 | 20 | 120 | 60 | 119.94 | 30.19 | 0.853 | 0.2358 | 41.696 | 21.176 | 28.388 | 0.6011 | -96.3605 | 70.4689 | 20 | 230 | 50 | 229.97 | 29.808 | 0.909 | 0.1326 | 30.814 | 21.186 | 28.313 | 0.5997 | -96.3701 | 65.9736 | 20 | 277 | 60 | 276.98 | 36.08 | 0.933 | 0.0934 | 25.667 | 21.179 | 28.364 | 0.6007 | -96.3636 | 64.3837
| 10 | 120 | 60 | 119.95 | 26.947 | 0.5276 | 0.1632 | 35.586 | 41.122 | 7.054 | 0.2901 | -99.0956 | 54.9848 | 10 | 230 | 50 | 229.97 | 28.532 | 0.556 | 0.0847 | 18.134 | 41.099 | 7.282 | 0.2993 | -99.0664 | 53.8309 | 10 | 277 | 60 | 276.98 | 35.09 | 0.57 | 0.0586 | 21.431 | 41.051 | 7.109 | 0.2918 | -99.0886 | 51.193 | 10 | 120 | 60 | 119.95 | 26.233 | 0.4337 | 0.1378 | 30.929 | 30.918 | 7.741 | 0.2393 | -99.0076 | 55.1764 | 10 | 239 | 50 | 238.97 | 28.691 | 0.453 | 0.066 | 22.426 | 30.913 | 7.641 | 0.2362 | -99.0204 | 52.1413 | 10 | 277 | 60 | 276.98 | 34.89 | 0.477 | 0.0493 | 19.208 | 30.921 | 7.66 | 0.2368 | -99.0179 | 49.6436 | 10 | 120 | 60 | 119.95 | 30.18 | 0.853 | 0.2356 | 47.607 | 21.18 | 28.346 | 0.6004 | -96.3659 | 70.3869 | 10 | 230 | 50 | 229.97 | 29.796 | 0.908 | 0.1325 | 25.173 | 21.191 | 28.275 | 0.5991 | -96.375 | 65.9802 | 10 | 277 | 60 | 276.98 | 36.05 | 0.932 | 0.0933 | 18.262 | 21.183 | 28.331 | 0.6001 | -96.3678 | 64.3884
| 0 | 120 | 60 | 119.95 | 24.592 | 0.0691 | 0.0234 | 18.34 | 35.736 | 0 | 0.00033 | -100 | 0.47757 | 0 | 230 | 50 | 229.97 | 27.576 | 0.183 | 0.0288 | 5.342 | 35.668 | 0 | 0.00032 | -100 | 0.17486 | 0 | 277 | 60 | 276.98 | 34.48 | 0.245 | 0.0256 | 18.754 | 35.61 | 0 | 0.00032 | -100 | 0.13061 | 0 | 120 | 60 | 119.95 | 24.573 | 0.0693 | 0.0235 | 36.582 | 26.569 | 0 | 0.00017 | -100 | 0.24531 | 0 | 239 | 50 | 238.97 | 28.101 | 0.192 | 0.0286 | 19.655 | 26.565 | 0 | 0.00017 | -100 | 0.088542 | 0 | 277 | 60 | 276.98 | 34.48 | 0.243 | 0.0254 | 6.172 | 26.571 | 0 | 0.00017 | -100 | 0.069959 | 0 | 120 | 60 | 119.95 | 24.618 | 0.0749 | 0.0253 | 9.397 | 17.646 | 0 | 0.0001 | -100 | 0.13351 | 0 | 230 | 50 | 229.97 | 27.605 | 0.181 | 0.0285 | 8.503 | 17.658 | 0 | 0.0001 | -100 | 0.055249 | 0 | 277 | 60 | 276.98 | 34.5 | 0.245 | 0.0256 | 6.561 | 17.644 | 0 | 9e-05 | -100 | 0.036735
s

## DALI I2C Dimming (Logarithmic)
DALI/Logarithmic I2C Dimming
DER-925 Unit 9
48V LED, 120 VAC | [12 empty] | 48V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
254 | [12 empty] | 254 | 230 | 50 | 229.83 | 188.57 | 41.401 | 0.9554 | 6.914 | 47.675 | 773.3 | 36.871 | -0.85897 | 89.0582 | 254
251 | [12 empty] | 251 | 230 | 50 | 229.84 | 174.21 | 38.033 | 0.9499 | 6.994 | 47.419 | 713.5 | 33.837 | -8.5256 | 88.9675 | 251
248 | [12 empty] | 248 | 230 | 50 | 229.85 | 161.14 | 34.943 | 0.9435 | 7.242 | 47.181 | 658.2 | 31.061 | -15.6154 | 88.8905 | 248
245 | [12 empty] | 245 | 230 | 50 | 229.85 | 149.26 | 32.147 | 0.9369 | 7.337 | 46.959 | 607.6 | 28.538 | -22.1026 | 88.7734 | 245
242 | [12 empty] | 242 | 230 | 50 | 229.86 | 138.48 | 29.552 | 0.9284 | 7.788 | 46.747 | 560.4 | 26.202 | -28.1538 | 88.664 | 242
239 | [12 empty] | 239 | 230 | 50 | 229.87 | 128.7 | 27.211 | 0.9197 | 8.161 | 46.542 | 516.8 | 24.058 | -33.7436 | 88.4128 | 239
236 | [12 empty] | 236 | 230 | 50 | 229.86 | 119.82 | 25.059 | 0.9096 | 8.483 | 46.353 | 477.1 | 22.119 | -38.8333 | 88.2677 | 236
233 | [12 empty] | 233 | 230 | 50 | 229.83 | 111.78 | 23.079 | 0.8983 | 8.956 | 46.176 | 440.3 | 20.337 | -43.5513 | 88.1191 | 233
230 | [12 empty] | 230 | 230 | 50 | 229.88 | 104.43 | 21.272 | 0.8861 | 9.465 | 46.007 | 406.3 | 18.697 | -47.9103 | 87.8949 | 230
227 | [12 empty] | 227 | 230 | 50 | 229.89 | 97.87 | 19.623 | 0.8723 | 10.186 | 45.844 | 375.2 | 17.202 | -51.8974 | 87.6624 | 227
224 | [12 empty] | 224 | 230 | 50 | 229.81 | 91.88 | 18.104 | 0.8575 | 11.034 | 45.692 | 346.3 | 15.826 | -55.6026 | 87.4171 | 224
221 | [12 empty] | 221 | 230 | 50 | 229.76 | 86.44 | 16.705 | 0.8412 | 11.808 | 45.544 | 319.6 | 14.557 | -59.0256 | 87.1416 | 221
218 | [12 empty] | 218 | 230 | 50 | 229.9 | 81.52 | 15.442 | 0.824 | 12.465 | 45.405 | 295.05 | 13.398 | -62.1731 | 86.7634 | 218
215 | [12 empty] | 215 | 230 | 50 | 229.91 | 77.01 | 14.263 | 0.8054 | 13.333 | 45.272 | 272.35 | 12.332 | -65.0833 | 86.4615 | 215
212 | [12 empty] | 212 | 230 | 50 | 229.92 | 73.01 | 13.186 | 0.7856 | 14.29 | 45.147 | 251.56 | 11.358 | -67.7487 | 86.1368 | 212
209 | [12 empty] | 209 | 230 | 50 | 229.92 | 69.29 | 12.19 | 0.7651 | 15.575 | 45.026 | 232.24 | 10.458 | -70.2256 | 85.7916 | 209
206 | [12 empty] | 206 | 230 | 50 | 229.92 | 65.98 | 11.271 | 0.7432 | 16.583 | 44.91 | 214.39 | 9.629 | -72.5141 | 85.4316 | 206
203 | [12 empty] | 203 | 230 | 50 | 229.92 | 62.9 | 10.428 | 0.7211 | 17.429 | 44.799 | 197.98 | 8.87 | -74.6179 | 85.0595 | 203
200 | [12 empty] | 200 | 230 | 50 | 229.87 | 60.16 | 9.659 | 0.6983 | 18.562 | 44.694 | 182.81 | 8.171 | -76.5628 | 84.5947 | 200
197 | [12 empty] | 197 | 230 | 50 | 229.81 | 57.68 | 8.939 | 0.6746 | 19.942 | 44.594 | 168.81 | 7.529 | -78.3577 | 84.2264 | 197
194 | [12 empty] | 194 | 230 | 50 | 229.85 | 89.07 | 7.507 | 0.3667 | 60.94 | 44.387 | 135.16 | 6 | -82.6718 | 79.9254 | 194
191 | [12 empty] | 191 | 230 | 50 | 229.83 | 82.25 | 6.976 | 0.368 | 56.439 | 44.303 | 125.39 | 5.555 | -83.9244 | 79.6302 | 191
188 | [12 empty] | 188 | 230 | 50 | 229.77 | 77.85 | 6.466 | 0.3619 | 50.966 | 44.219 | 116.13 | 5.135 | -85.1115 | 79.4154 | 188
185 | [12 empty] | 185 | 230 | 50 | 229.87 | 75.33 | 6.014 | 0.3472 | 51.355 | 44.139 | 107.63 | 4.75 | -86.2013 | 78.9824 | 185
182 | [12 empty] | 182 | 230 | 50 | 229.84 | 69.4 | 5.527 | 0.3466 | 47.566 | 44.045 | 98.55 | 4.341 | -87.3654 | 78.5417 | 182
179 | [12 empty] | 179 | 230 | 50 | 229.85 | 66.51 | 5.193 | 0.3395 | 46.518 | 43.983 | 92.34 | 4.061 | -88.1615 | 78.2014 | 179
176 | [12 empty] | 176 | 230 | 50 | 229.9 | 61.37 | 4.788 | 0.3393 | 45.186 | 43.901 | 84.76 | 3.721 | -89.1333 | 77.7151 | 176
173 | [12 empty] | 173 | 230 | 50 | 229.9 | 57.88 | 4.458 | 0.3346 | 44.295 | 43.831 | 78.52 | 3.442 | -89.9333 | 77.2095 | 173
170 | [12 empty] | 170 | 230 | 50 | 229.87 | 54.16 | 4.134 | 0.3321 | 44.229 | 43.759 | 72.45 | 3.17 | -90.7115 | 76.6812 | 170
167 | [12 empty] | 167 | 230 | 50 | 229.84 | 51.24 | 3.875 | 0.3288 | 42.58 | 43.699 | 67.52 | 2.951 | -91.3436 | 76.1548 | 167
164 | [12 empty] | 164 | 230 | 50 | 229.86 | 48.52 | 3.598 | 0.3226 | 41.996 | 43.631 | 62.3 | 2.718 | -92.0128 | 75.542 | 164
161 | [12 empty] | 161 | 230 | 50 | 229.84 | 45.13 | 3.337 | 0.3218 | 41.449 | 43.563 | 57.35 | 2.4983 | -92.6474 | 74.8666 | 161
158 | [12 empty] | 158 | 230 | 50 | 229.91 | 43.18 | 3.111 | 0.3134 | 40.721 | 43.502 | 53.08 | 2.309 | -93.1949 | 74.2205 | 158
155 | [12 empty] | 155 | 230 | 50 | 229.94 | 39.75 | 2.752 | 0.301 | 37.868 | 43.378 | 45.46 | 1.9722 | -94.1718 | 71.6642 | 155
152 | [12 empty] | 152 | 230 | 50 | 229.94 | 39.2 | 2.688 | 0.2982 | 39.281 | 43.362 | 44.3 | 1.921 | -94.3205 | 71.4658 | 152
149 | [12 empty] | 149 | 230 | 50 | 229.94 | 36.74 | 2.442 | 0.2891 | 37.427 | 43.277 | 39.6 | 1.7136 | -94.9231 | 70.172 | 149
146 | [12 empty] | 146 | 230 | 50 | 229.94 | 35.62 | 2.301 | 0.2809 | 37.445 | 43.228 | 36.97 | 1.5983 | -95.2603 | 69.4611 | 146
143 | [12 empty] | 143 | 230 | 50 | 229.95 | 34.35 | 2.135 | 0.2703 | 36.051 | 43.164 | 33.75 | 1.4569 | -95.6731 | 68.2389 | 143
140 | [12 empty] | 140 | 230 | 50 | 229.94 | 33.59 | 2.012 | 0.2605 | 35.805 | 43.115 | 31.42 | 1.3547 | -95.9718 | 67.331 | 140
137 | [12 empty] | 137 | 230 | 50 | 229.95 | 32.65 | 1.886 | 0.2512 | 34.686 | 43.063 | 29.054 | 1.2512 | -96.2751 | 66.3415 | 137
134 | [12 empty] | 134 | 230 | 50 | 229.95 | 31.75 | 1.773 | 0.2429 | 34.302 | 43.013 | 26.953 | 1.1593 | -96.5445 | 65.3864 | 134
131 | [12 empty] | 131 | 230 | 50 | 229.94 | 30.88 | 1.652 | 0.2327 | 33.422 | 42.956 | 24.726 | 1.0621 | -96.83 | 64.2918 | 131
128 | [12 empty] | 128 | 230 | 50 | 229.94 | 30.31 | 1.549 | 0.2222 | 32.246 | 42.907 | 22.942 | 0.9844 | -97.0587 | 63.5507 | 128
125 | [12 empty] | 125 | 230 | 50 | 229.94 | 29.8 | 1.45 | 0.2116 | 31.694 | 42.858 | 21.239 | 0.9102 | -97.2771 | 62.7724 | 125
122 | [12 empty] | 122 | 230 | 50 | 229.93 | 29.189 | 1.331 | 0.1983 | 31.347 | 42.793 | 19.233 | 0.8231 | -97.5342 | 61.8407 | 122
119 | [12 empty] | 119 | 230 | 50 | 229.92 | 28.791 | 1.253 | 0.1893 | 30.706 | 42.749 | 17.894 | 0.7649 | -97.7059 | 61.0455 | 119
116 | [12 empty] | 116 | 230 | 50 | 229.93 | 28.312 | 1.156 | 0.1775 | 29.398 | 42.687 | 16.227 | 0.6927 | -97.9196 | 59.9221 | 116
113 | [12 empty] | 113 | 230 | 50 | 229.94 | 27.988 | 1.09 | 0.1694 | 28.719 | 42.644 | 15.119 | 0.6447 | -98.0617 | 59.1468 | 113
110 | [12 empty] | 110 | 230 | 50 | 229.95 | 27.654 | 1.019 | 0.1603 | 26.962 | 42.593 | 13.898 | 0.592 | -98.2182 | 58.0962 | 110
107 | [12 empty] | 107 | 230 | 50 | 229.95 | 27.734 | 1.04 | 0.1631 | 27.713 | 42.576 | 13.472 | 0.5736 | -98.2728 | 55.1538 | 107
104 | [12 empty] | 104 | 230 | 50 | 229.95 | 27.355 | 0.954 | 0.1517 | 26.698 | 42.512 | 12.158 | 0.5168 | -98.4413 | 54.1719 | 104
101 | [12 empty] | 101 | 230 | 50 | 229.94 | 27.033 | 0.881 | 0.1417 | 25.582 | 42.445 | 10.92 | 0.4635 | -98.6 | 52.6107 | 101
98 | [12 empty] | 98 | 230 | 50 | 229.94 | 26.709 | 0.802 | 0.1306 | 25.438 | 42.363 | 9.563 | 0.4051 | -98.774 | 50.5112 | 98
95 | [12 empty] | 95 | 230 | 50 | 229.94 | 26.464 | 0.747 | 0.1228 | 22.935 | 42.305 | 8.676 | 0.367 | -98.8877 | 49.1299 | 95
92 | [12 empty] | 92 | 230 | 50 | 229.94 | 26.353 | 0.716 | 0.1182 | 23.218 | 42.27 | 8.186 | 0.346 | -98.9505 | 48.324 | 92
89 | [12 empty] | 89 | 230 | 50 | 229.94 | 26.229 | 0.686 | 0.1137 | 22.471 | 42.234 | 7.706 | 0.3254 | -99.0121 | 47.4344 | 89
86 | [12 empty] | 86 | 230 | 50 | 229.94 | 26.234 | 0.685 | 0.1136 | 22.517 | 42.236 | 7.705 | 0.3254 | -99.0122 | 47.5036 | 86
83 | [12 empty] | 83 | 230 | 50 | 229.95 | 26.229 | 0.685 | 0.1136 | 22.616 | 42.238 | 7.705 | 0.3254 | -99.0122 | 47.5036 | 83
80 | [12 empty] | 80 | 230 | 50 | 229.94 | 26.228 | 0.686 | 0.1137 | 22.364 | 42.239 | 7.703 | 0.3254 | -99.0124 | 47.4344 | 80
77 | [12 empty] | 77 | 230 | 50 | 229.94 | 26.231 | 0.686 | 0.1137 | 22.345 | 42.241 | 7.703 | 0.3254 | -99.0124 | 47.4344 | 77
74 | [12 empty] | 74 | 230 | 50 | 229.94 | 26.228 | 0.686 | 0.1137 | 21.873 | 42.243 | 7.703 | 0.3254 | -99.0124 | 47.4344 | 74
71 | [12 empty] | 71 | 230 | 50 | 229.94 | 26.223 | 0.685 | 0.1136 | 22.832 | 42.244 | 7.703 | 0.3254 | -99.0124 | 47.5036 | 71
68 | [12 empty] | 68 | 230 | 50 | 229.94 | 26.222 | 0.685 | 0.1136 | 21.48 | 42.246 | 7.703 | 0.3254 | -99.0124 | 47.5036 | 68
65 | [12 empty] | 65 | 230 | 50 | 229.94 | 26.218 | 0.686 | 0.1137 | 22.587 | 42.247 | 7.702 | 0.3254 | -99.0126 | 47.4344 | 65
62 | [12 empty] | 62 | 230 | 50 | 229.94 | 26.221 | 0.685 | 0.1136 | 22.356 | 42.248 | 7.701 | 0.3254 | -99.0127 | 47.5036 | 62
59 | [12 empty] | 59 | 230 | 50 | 229.94 | 26.238 | 0.685 | 0.1136 | 22.292 | 42.249 | 7.701 | 0.3254 | -99.0127 | 47.5036 | 59
56 | [12 empty] | 56 | 230 | 50 | 229.94 | 26.233 | 0.686 | 0.1137 | 22.647 | 42.251 | 7.702 | 0.3254 | -99.0126 | 47.4344 | 56
53 | [12 empty] | 53 | 230 | 50 | 229.94 | 26.233 | 0.685 | 0.1136 | 22.387 | 42.251 | 7.7 | 0.3253 | -99.0128 | 47.4891 | 53
50 | [12 empty] | 50 | 230 | 50 | 229.94 | 26.224 | 0.686 | 0.1138 | 20.335 | 42.252 | 7.7 | 0.3253 | -99.0128 | 47.4198 | 50
47 | [12 empty] | 47 | 230 | 50 | 229.94 | 26.226 | 0.685 | 0.1136 | 20.267 | 42.253 | 7.7 | 0.3254 | -99.0128 | 47.5036 | 47
44 | [12 empty] | 44 | 230 | 50 | 229.94 | 26.23 | 0.685 | 0.1136 | 21.079 | 42.254 | 7.7 | 0.3253 | -99.0128 | 47.4891 | 44
41 | [12 empty] | 41 | 230 | 50 | 229.94 | 26.226 | 0.684 | 0.1135 | 21.311 | 42.255 | 7.7 | 0.3254 | -99.0128 | 47.5731 | 41
38 | [12 empty] | 38 | 230 | 50 | 229.94 | 26.228 | 0.685 | 0.1136 | 21.108 | 42.255 | 7.699 | 0.3253 | -99.0129 | 47.4891 | 38
35 | [12 empty] | 35 | 230 | 50 | 229.94 | 26.219 | 0.685 | 0.1137 | 20.633 | 42.256 | 7.7 | 0.3254 | -99.0128 | 47.5036 | 35
32 | [12 empty] | 32 | 230 | 50 | 229.94 | 26.223 | 0.684 | 0.1135 | 20.288 | 42.257 | 7.7 | 0.3254 | -99.0128 | 47.5731 | 32
29 | [12 empty] | 29 | 230 | 50 | 229.94 | 26.217 | 0.685 | 0.1137 | 20.486 | 42.258 | 7.7 | 0.3254 | -99.0128 | 47.5036 | 29
26 | [12 empty] | 26 | 230 | 50 | 229.94 | 26.23 | 0.685 | 0.1136 | 20.861 | 42.259 | 7.699 | 0.3254 | -99.0129 | 47.5036 | 26
23 | [12 empty] | 23 | 230 | 50 | 229.94 | 26.229 | 0.685 | 0.1137 | 21.295 | 42.259 | 7.7 | 0.3254 | -99.0128 | 47.5036 | 23
20 | [12 empty] | 20 | 230 | 50 | 229.94 | 26.233 | 0.686 | 0.1137 | 19.868 | 42.26 | 7.699 | 0.3254 | -99.0129 | 47.4344 | 20
17 | [12 empty] | 17 | 230 | 50 | 229.94 | 26.236 | 0.686 | 0.1137 | 20.756 | 42.26 | 7.7 | 0.3254 | -99.0128 | 47.4344 | 17
14 | [12 empty] | 14 | 230 | 50 | 229.94 | 26.232 | 0.686 | 0.1137 | 20.563 | 42.261 | 7.7 | 0.3254 | -99.0128 | 47.4344 | 14
11 | [12 empty] | 11 | 230 | 50 | 229.94 | 26.238 | 0.686 | 0.1137 | 20.651 | 42.261 | 7.699 | 0.3254 | -99.0129 | 47.4344 | 11
8 | [12 empty] | 8 | 230 | 50 | 229.94 | 26.222 | 0.685 | 0.1136 | 20.263 | 42.262 | 7.7 | 0.3254 | -99.0128 | 47.5036 | 8
5 | [12 empty] | 5 | 230 | 50 | 229.94 | 26.223 | 0.686 | 0.1137 | 21.102 | 42.262 | 7.699 | 0.3254 | -99.0129 | 47.4344 | 5
2 | [12 empty] | 2 | 230 | 50 | 229.94 | 26.239 | 0.686 | 0.1137 | 19.547 | 42.263 | 7.7 | 0.3254 | -99.0128 | 47.4344 | 2
0 | [12 empty] | 0 | 230 | 50 | 229.94 | 24.719 | 0.19 | 0.0335 | 7.48 | 37.924 | 0.0757 | 0.00287 | -99.9903 | 1.5105 | 0

## I2C Dimming (Linear)
Linear I2C Dimming
DER-925 Unit 9
48V LED, 120 VAC | [12 empty] | 46V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
254 | 120 | 60 | 119.88 | 348.21 | 41.3 | 0.9895 | 6.297 | 47.641 | 768.8 | 36.593 | -1.4359 | 88.6029 | [13 empty] | 254 | 277 | 60 | 276.87 | 164.55 | 41.057 | 0.9011 | 9.771 | 47.587 | 770.6 | 36.635 | -1.2051 | 89.2296 | 254 | 120 | 60 | 119.82 | 179.29 | 20.961 | 0.9756 | 4.898 | 23.713 | 768.8 | 18.212 | -1.4359 | 86.8852 | [13 empty] | 254 | 277 | 60 | 276.93 | 100.39 | 21.213 | 0.763 | 17.612 | 23.737 | 769.9 | 18.254 | -1.2949 | 86.051
249 | 120 | 60 | 119.89 | 339.57 | 40.36 | 0.9914 | 4.458 | 47.555 | 752.8 | 35.766 | -3.4872 | 88.6174 | [13 empty] | 249 | 277 | 60 | 276.88 | 161.41 | 40.136 | 0.8982 | 9.525 | 47.501 | 754.5 | 35.803 | -3.2692 | 89.2042 | 249 | 120 | 60 | 119.83 | 175.34 | 20.479 | 0.9747 | 5.369 | 23.674 | 752.7 | 17.803 | -3.5 | 86.933 | [13 empty] | 249 | 277 | 60 | 276.93 | 98.89 | 20.749 | 0.7576 | 17.15 | 23.698 | 753.9 | 17.847 | -3.3462 | 86.0138
244 | 120 | 60 | 119.89 | 332.08 | 39.48 | 0.9915 | 3.875 | 47.472 | 737.7 | 34.989 | -5.4231 | 88.6246 | [13 empty] | 244 | 277 | 60 | 276.88 | 158.5 | 39.287 | 0.8953 | 9.982 | 47.418 | 739.3 | 35.023 | -5.2179 | 89.1465 | 244 | 120 | 60 | 119.83 | 171.78 | 20.044 | 0.9737 | 5.539 | 23.639 | 738 | 17.427 | -5.3846 | 86.9437 | [13 empty] | 244 | 277 | 60 | 276.93 | 97.47 | 20.301 | 0.7521 | 17.619 | 23.663 | 739 | 17.469 | -5.2564 | 86.0499
239 | 120 | 60 | 119.89 | 324.61 | 38.59 | 0.9915 | 3.677 | 47.389 | 722.7 | 34.217 | -7.3462 | 88.668 | [13 empty] | 239 | 277 | 60 | 276.89 | 155.57 | 38.422 | 0.892 | 9.489 | 47.337 | 724.4 | 34.256 | -7.1282 | 89.1573 | 239 | 120 | 60 | 119.83 | 168.28 | 19.612 | 0.9725 | 5.695 | 23.604 | 723.1 | 17.051 | -7.2949 | 86.9417 | [13 empty] | 239 | 277 | 60 | 276.93 | 96.1 | 19.866 | 0.7465 | 18.119 | 23.627 | 724.1 | 17.089 | -7.1667 | 86.0213
234 | 120 | 60 | 119.89 | 317.09 | 37.68 | 0.9912 | 3.645 | 47.303 | 707 | 33.41 | -9.359 | 88.6677 | [13 empty] | 234 | 277 | 60 | 276.88 | 152.66 | 37.554 | 0.8884 | 10.009 | 47.255 | 709.1 | 33.478 | -9.0897 | 89.1463 | 234 | 120 | 60 | 119.84 | 164.75 | 19.179 | 0.9714 | 5.334 | 23.569 | 708.2 | 16.674 | -9.2051 | 86.9388 | [13 empty] | 234 | 277 | 60 | 276.93 | 94.76 | 19.436 | 0.7406 | 19.042 | 23.591 | 709.1 | 16.709 | -9.0897 | 85.9693
229 | 120 | 60 | 119.89 | 309.93 | 36.81 | 0.9906 | 4.15 | 47.219 | 691.9 | 32.641 | -11.2949 | 88.6743 | [13 empty] | 229 | 277 | 60 | 276.89 | 149.64 | 36.678 | 0.8851 | 9.907 | 47.169 | 693.4 | 32.676 | -11.1026 | 89.0888 | 229 | 120 | 60 | 119.84 | 161.22 | 18.746 | 0.9703 | 5.352 | 23.534 | 693.3 | 16.3 | -11.1154 | 86.9519 | [13 empty] | 229 | 277 | 60 | 276.93 | 93.42 | 18.999 | 0.7344 | 19.478 | 23.555 | 694 | 16.331 | -11.0256 | 85.9572
224 | 120 | 60 | 119.89 | 302.89 | 35.95 | 0.99 | 4.068 | 47.137 | 677 | 31.883 | -13.2051 | 88.6871 | [13 empty] | 224 | 277 | 60 | 276.89 | 146.83 | 35.826 | 0.8812 | 10.385 | 47.087 | 678.4 | 31.914 | -13.0256 | 89.0806 | 224 | 120 | 60 | 119.84 | 157.67 | 18.315 | 0.9693 | 5.068 | 23.499 | 678.4 | 15.925 | -13.0256 | 86.9506 | [13 empty] | 224 | 277 | 60 | 276.93 | 92.09 | 18.566 | 0.728 | 18.769 | 23.519 | 679.1 | 15.955 | -12.9359 | 85.9367
219 | 120 | 60 | 119.89 | 295.98 | 35.11 | 0.9892 | 4.222 | 47.054 | 662.1 | 31.127 | -15.1154 | 88.6557 | [13 empty] | 219 | 277 | 60 | 276.89 | 144.03 | 34.986 | 0.8773 | 10.649 | 47.004 | 663.5 | 31.154 | -14.9359 | 89.047 | 219 | 120 | 60 | 119.84 | 154.08 | 17.879 | 0.9683 | 5.742 | 23.462 | 663.4 | 15.549 | -14.9487 | 86.968 | [13 empty] | 219 | 277 | 60 | 276.93 | 90.78 | 18.141 | 0.7216 | 19.906 | 23.483 | 664.2 | 15.58 | -14.8462 | 85.8828
214 | 120 | 60 | 119.89 | 289.02 | 34.26 | 0.9888 | 3.619 | 46.971 | 647.4 | 30.381 | -17 | 88.6778 | [13 empty] | 214 | 277 | 60 | 276.89 | 141.21 | 34.144 | 0.8731 | 11.129 | 46.92 | 648.5 | 30.396 | -16.859 | 89.023 | 214 | 120 | 60 | 119.85 | 150.53 | 17.445 | 0.967 | 5.858 | 23.427 | 648.4 | 15.175 | -16.8718 | 86.9877 | [13 empty] | 214 | 277 | 60 | 276.94 | 89.41 | 17.704 | 0.715 | 19.237 | 23.447 | 649.1 | 15.202 | -16.7821 | 85.8676
209 | 120 | 60 | 119.9 | 282.11 | 33.43 | 0.9884 | 4.335 | 46.889 | 632.9 | 29.647 | -18.859 | 88.6838 | [13 empty] | 209 | 277 | 60 | 276.89 | 138.42 | 33.305 | 0.8689 | 11.18 | 46.835 | 633.4 | 29.636 | -18.7949 | 88.9836 | 209 | 120 | 60 | 119.85 | 147.01 | 17.013 | 0.9656 | 5.377 | 23.39 | 633.5 | 14.802 | -18.7821 | 87.0041 | [13 empty] | 209 | 277 | 60 | 276.94 | 88.11 | 17.278 | 0.7081 | 19.628 | 23.41 | 634.1 | 14.828 | -18.7051 | 85.8201
204 | 120 | 60 | 119.9 | 274.8 | 32.57 | 0.9884 | 4.113 | 46.803 | 617.8 | 28.89 | -20.7949 | 88.7013 | [13 empty] | 204 | 277 | 60 | 276.9 | 135.62 | 32.472 | 0.8646 | 11.377 | 46.751 | 618.5 | 28.884 | -20.7051 | 88.9505 | 204 | 120 | 60 | 119.85 | 143.56 | 16.588 | 0.9642 | 5.453 | 23.353 | 618.5 | 14.429 | -20.7051 | 86.9846 | [13 empty] | 204 | 277 | 60 | 276.94 | 86.77 | 16.855 | 0.7014 | 19.975 | 23.373 | 619.2 | 14.455 | -20.6154 | 85.7609
199 | 120 | 60 | 119.9 | 267.52 | 31.7 | 0.9883 | 3.483 | 46.717 | 602.8 | 28.132 | -22.7179 | 88.7445 | [13 empty] | 199 | 277 | 60 | 276.9 | 132.91 | 31.639 | 0.8598 | 11.4 | 46.667 | 603.5 | 28.136 | -22.6282 | 88.9282 | 199 | 120 | 60 | 119.85 | 140.14 | 16.168 | 0.9626 | 5.45 | 23.317 | 603.7 | 14.061 | -22.6026 | 86.9681 | [13 empty] | 199 | 277 | 60 | 276.94 | 85.47 | 16.429 | 0.694 | 21.218 | 23.336 | 604.3 | 14.087 | -22.5256 | 85.7447
194 | 120 | 60 | 119.9 | 260.6 | 30.87 | 0.9879 | 3.585 | 46.631 | 587.7 | 27.38 | -24.6538 | 88.6945 | [13 empty] | 194 | 277 | 60 | 276.9 | 130.24 | 30.815 | 0.8546 | 12.201 | 46.582 | 588.6 | 27.391 | -24.5385 | 88.8885 | 194 | 120 | 60 | 119.86 | 136.68 | 15.744 | 0.961 | 4.998 | 23.28 | 588.8 | 13.693 | -24.5128 | 86.9728 | [13 empty] | 194 | 277 | 60 | 276.94 | 84.18 | 16.002 | 0.6864 | 21.473 | 23.299 | 589.2 | 13.714 | -24.4615 | 85.7018
189 | 120 | 60 | 119.9 | 253.75 | 30.04 | 0.9873 | 3.599 | 46.546 | 573 | 26.646 | -26.5385 | 88.7017 | [13 empty] | 189 | 277 | 60 | 276.9 | 127.59 | 30.007 | 0.8493 | 11.518 | 46.497 | 573.8 | 26.655 | -26.4359 | 88.8293 | 189 | 120 | 60 | 119.86 | 133.32 | 15.324 | 0.959 | 5.225 | 23.244 | 574.1 | 13.329 | -26.3974 | 86.9812 | [13 empty] | 189 | 277 | 60 | 276.94 | 82.96 | 15.592 | 0.6787 | 21.611 | 23.263 | 574.5 | 13.35 | -26.3462 | 85.6208
184 | 120 | 60 | 119.9 | 246.93 | 29.21 | 0.9866 | 3.655 | 46.459 | 558.1 | 25.906 | -28.4487 | 88.6888 | [13 empty] | 184 | 277 | 60 | 276.91 | 124.93 | 29.185 | 0.8438 | 11.673 | 46.409 | 558.7 | 25.9 | -28.3718 | 88.7442 | 184 | 120 | 60 | 119.86 | 129.95 | 14.902 | 0.9568 | 6.322 | 23.205 | 559.1 | 12.96 | -28.3205 | 86.9682 | [13 empty] | 184 | 277 | 60 | 276.94 | 81.66 | 15.17 | 0.6708 | 21.964 | 23.225 | 559.5 | 12.981 | -28.2692 | 85.5702
179 | 120 | 60 | 119.9 | 240.22 | 28.39 | 0.9856 | 4.144 | 46.371 | 543.3 | 25.172 | -30.3462 | 88.665 | [13 empty] | 179 | 277 | 60 | 276.91 | 122.23 | 28.349 | 0.8376 | 12.082 | 46.321 | 543.7 | 25.163 | -30.2949 | 88.7615 | 179 | 120 | 60 | 119.86 | 126.54 | 14.482 | 0.9547 | 6.285 | 23.167 | 544.1 | 12.592 | -30.2436 | 86.9493 | [13 empty] | 179 | 277 | 60 | 276.94 | 80.37 | 14.745 | 0.6625 | 21.757 | 23.187 | 544.6 | 12.614 | -30.1795 | 85.5476
174 | 120 | 60 | 119.9 | 233.15 | 27.52 | 0.9846 | 4.356 | 46.277 | 527.5 | 24.388 | -32.3718 | 88.6192 | [13 empty] | 174 | 277 | 60 | 276.91 | 119.6 | 27.543 | 0.8316 | 13.01 | 46.233 | 528.9 | 24.43 | -32.1923 | 88.6977 | 174 | 120 | 60 | 119.86 | 123.2 | 14.067 | 0.9527 | 6.573 | 23.129 | 529.2 | 12.228 | -32.1538 | 86.9269 | [13 empty] | 174 | 277 | 60 | 276.94 | 79.12 | 14.329 | 0.6539 | 22.046 | 23.149 | 529.7 | 12.249 | -32.0897 | 85.484
169 | 120 | 60 | 119.91 | 225.99 | 26.66 | 0.984 | 3.839 | 46.186 | 512.4 | 23.643 | -34.3077 | 88.6834 | [13 empty] | 169 | 277 | 60 | 276.91 | 117.01 | 26.732 | 0.8251 | 12.741 | 46.144 | 513.9 | 23.692 | -34.1154 | 88.6279 | 169 | 120 | 60 | 119.87 | 119.79 | 13.649 | 0.9506 | 6.84 | 23.089 | 514.3 | 11.862 | -34.0641 | 86.9075 | [13 empty] | 169 | 277 | 60 | 276.94 | 77.86 | 13.911 | 0.6452 | 22.784 | 23.11 | 514.6 | 11.881 | -34.0256 | 85.4072
164 | 120 | 60 | 119.91 | 219.19 | 25.85 | 0.9834 | 3.404 | 46.097 | 497.7 | 22.92 | -36.1923 | 88.6654 | [13 empty] | 164 | 277 | 60 | 276.91 | 114.42 | 25.921 | 0.8181 | 12.981 | 46.055 | 498.9 | 22.954 | -36.0385 | 88.5537 | 164 | 120 | 60 | 119.87 | 116.41 | 13.229 | 0.948 | 5.639 | 23.05 | 499.4 | 11.5 | -35.9744 | 86.9302 | [13 empty] | 164 | 277 | 60 | 276.94 | 76.6 | 13.49 | 0.6359 | 23.691 | 23.071 | 499.6 | 11.514 | -35.9487 | 85.3521
159 | 120 | 60 | 119.91 | 212.79 | 25.08 | 0.9828 | 4.1 | 46.009 | 483.3 | 22.218 | -38.0385 | 88.5885 | [13 empty] | 159 | 277 | 60 | 276.92 | 111.85 | 25.114 | 0.8108 | 13.845 | 45.964 | 483.9 | 22.219 | -37.9615 | 88.4726 | 159 | 120 | 60 | 119.87 | 113.13 | 12.814 | 0.9449 | 5.862 | 23.011 | 484.3 | 11.134 | -37.9103 | 86.8893 | [13 empty] | 159 | 277 | 60 | 276.95 | 75.36 | 13.079 | 0.6267 | 24.694 | 23.031 | 484.6 | 11.149 | -37.8718 | 85.2435
154 | 120 | 60 | 119.91 | 206.02 | 24.26 | 0.9821 | 4.384 | 45.918 | 468.4 | 21.488 | -39.9487 | 88.5738 | [13 empty] | 154 | 277 | 60 | 276.92 | 109.3 | 24.307 | 0.803 | 14.366 | 45.872 | 468.8 | 21.485 | -39.8974 | 88.3902 | 154 | 120 | 60 | 119.88 | 109.84 | 12.396 | 0.9415 | 6.182 | 22.971 | 469.3 | 10.769 | -39.8333 | 86.8748 | [13 empty] | 154 | 277 | 60 | 276.95 | 74.11 | 12.657 | 0.6166 | 24.826 | 22.99 | 469.5 | 10.783 | -39.8077 | 85.194
149 | 120 | 60 | 119.91 | 199.34 | 23.46 | 0.9811 | 3.491 | 45.825 | 453.5 | 20.763 | -41.859 | 88.5038 | [13 empty] | 149 | 277 | 60 | 276.92 | 106.79 | 23.505 | 0.7948 | 14.504 | 45.781 | 453.9 | 20.758 | -41.8077 | 88.3131 | 149 | 120 | 60 | 119.88 | 106.55 | 11.986 | 0.9383 | 6.301 | 22.931 | 454.3 | 10.406 | -41.7564 | 86.818 | [13 empty] | 149 | 277 | 60 | 276.95 | 72.84 | 12.238 | 0.6067 | 24.574 | 22.95 | 454.3 | 10.414 | -41.7564 | 85.0956
144 | 120 | 60 | 119.91 | 192.42 | 22.6 | 0.9794 | 3.555 | 45.728 | 438 | 20.006 | -43.8462 | 88.5221 | [13 empty] | 144 | 277 | 60 | 276.92 | 104.26 | 22.702 | 0.7862 | 15.22 | 45.688 | 438.8 | 20.029 | -43.7436 | 88.2257 | 144 | 120 | 60 | 119.88 | 103.25 | 11.57 | 0.9348 | 7.809 | 22.891 | 439.1 | 10.042 | -43.7051 | 86.7934 | [13 empty] | 144 | 277 | 60 | 276.95 | 71.6 | 11.822 | 0.5962 | 24.854 | 22.909 | 439.1 | 10.049 | -43.7051 | 85.0025
139 | 120 | 60 | 119.91 | 185.58 | 21.76 | 0.9778 | 3.597 | 45.632 | 422.9 | 19.276 | -45.7821 | 88.5846 | [13 empty] | 139 | 277 | 60 | 276.92 | 101.8 | 21.904 | 0.7771 | 15.128 | 45.593 | 423.9 | 19.307 | -45.6538 | 88.1437 | 139 | 120 | 60 | 119.88 | 99.92 | 11.149 | 0.9308 | 7.329 | 22.849 | 423.8 | 9.673 | -45.6667 | 86.7611 | [13 empty] | 139 | 277 | 60 | 276.95 | 70.38 | 11.408 | 0.5853 | 25.698 | 22.867 | 424.1 | 9.686 | -45.6282 | 84.9053
134 | 120 | 60 | 119.91 | 179.49 | 21.02 | 0.9766 | 4.948 | 45.541 | 408.7 | 18.594 | -47.6026 | 88.4586 | [13 empty] | 134 | 277 | 60 | 276.93 | 99.35 | 21.1 | 0.767 | 15.311 | 45.497 | 408.8 | 18.58 | -47.5897 | 88.0569 | 134 | 120 | 60 | 119.88 | 96.75 | 10.741 | 0.9261 | 6.807 | 22.808 | 408.8 | 9.313 | -47.5897 | 86.7051 | [13 empty] | 134 | 277 | 60 | 276.95 | 69.18 | 10.998 | 0.574 | 26.329 | 22.825 | 409.1 | 9.327 | -47.5513 | 84.8063
129 | 120 | 60 | 119.92 | 172.85 | 20.22 | 0.9754 | 3.725 | 45.444 | 393.7 | 17.875 | -49.5256 | 88.4026 | [13 empty] | 129 | 277 | 60 | 276.93 | 96.89 | 20.311 | 0.757 | 16.125 | 45.401 | 393.9 | 17.864 | -49.5 | 87.9523 | 129 | 120 | 60 | 119.89 | 93.6 | 10.333 | 0.9208 | 6.814 | 22.766 | 393.8 | 8.956 | -49.5128 | 86.6738 | [13 empty] | 129 | 277 | 60 | 276.95 | 67.98 | 10.596 | 0.5628 | 28.081 | 22.782 | 394.1 | 8.968 | -49.4744 | 84.6357
124 | 120 | 60 | 119.92 | 166.32 | 19.43 | 0.9741 | 3.618 | 45.346 | 378.7 | 17.159 | -51.4487 | 88.3119 | [13 empty] | 124 | 277 | 60 | 276.93 | 94.54 | 19.523 | 0.7458 | 17.499 | 45.304 | 378.8 | 17.146 | -51.4359 | 87.8246 | 124 | 120 | 60 | 119.89 | 90.5 | 9.932 | 0.9154 | 7.017 | 22.724 | 379 | 8.602 | -51.4103 | 86.6089 | [13 empty] | 124 | 277 | 60 | 276.95 | 66.8 | 10.188 | 0.5507 | 28.316 | 22.74 | 379.2 | 8.614 | -51.3846 | 84.5505
119 | 120 | 60 | 119.92 | 159.48 | 18.58 | 0.9717 | 4.508 | 45.243 | 363.2 | 16.415 | -53.4359 | 88.3477 | [13 empty] | 119 | 277 | 60 | 276.93 | 92.15 | 18.747 | 0.7346 | 18.033 | 45.206 | 364 | 16.439 | -53.3333 | 87.6887 | 119 | 120 | 60 | 119.89 | 87.39 | 9.528 | 0.9094 | 7.227 | 22.681 | 364 | 8.248 | -53.3333 | 86.5659 | [13 empty] | 119 | 277 | 60 | 276.95 | 65.6 | 9.788 | 0.5387 | 29.126 | 22.697 | 364.3 | 8.26 | -53.2949 | 84.389
114 | 120 | 60 | 119.92 | 153.31 | 17.81 | 0.9686 | 5.094 | 45.145 | 348.5 | 15.72 | -55.3205 | 88.265 | [13 empty] | 114 | 277 | 60 | 276.93 | 89.81 | 17.962 | 0.7222 | 18.333 | 45.107 | 349 | 15.729 | -55.2564 | 87.5682 | 114 | 120 | 60 | 119.89 | 84.26 | 9.123 | 0.9031 | 9.118 | 22.637 | 349.1 | 7.893 | -55.2436 | 86.5176 | [13 empty] | 114 | 277 | 60 | 276.95 | 64.48 | 9.387 | 0.5257 | 28.331 | 22.652 | 349.3 | 7.906 | -55.2179 | 84.2229
109 | 120 | 60 | 119.85 | 147.21 | 17.066 | 0.9672 | 3.979 | 45.047 | 334.2 | 15.04 | -57.1538 | 88.1284 | [13 empty] | 109 | 277 | 60 | 276.94 | 87.53 | 17.185 | 0.709 | 18.352 | 45.006 | 334.1 | 15.022 | -57.1667 | 87.4134 | 109 | 120 | 60 | 119.9 | 81.23 | 8.723 | 0.8957 | 8.963 | 22.592 | 334.2 | 7.542 | -57.1538 | 86.4611 | [13 empty] | 109 | 277 | 60 | 276.96 | 63.27 | 8.985 | 0.5127 | 29.033 | 22.607 | 334.4 | 7.554 | -57.1282 | 84.0735
104 | 120 | 60 | 119.85 | 140.71 | 16.28 | 0.9652 | 4.597 | 44.944 | 319.2 | 14.333 | -59.0769 | 88.0405 | [13 empty] | 104 | 277 | 60 | 276.94 | 85.19 | 16.407 | 0.6954 | 18.994 | 44.903 | 319.2 | 14.319 | -59.0769 | 87.2737 | 104 | 120 | 60 | 119.9 | 78.26 | 8.324 | 0.8871 | 9.521 | 22.547 | 319.2 | 7.19 | -59.0769 | 86.3767 | [13 empty] | 104 | 277 | 60 | 276.96 | 62.08 | 8.584 | 0.4993 | 29.716 | 22.562 | 319.4 | 7.2 | -59.0513 | 83.877
99 | 120 | 60 | 119.86 | 133.99 | 15.451 | 0.9623 | 4.696 | 44.833 | 303.6 | 13.598 | -61.0769 | 88.0072 | [13 empty] | 99 | 277 | 60 | 276.94 | 82.92 | 15.635 | 0.6808 | 19.665 | 44.798 | 304.2 | 13.614 | -61 | 87.0739 | 99 | 120 | 60 | 119.9 | 75.3 | 7.924 | 0.8777 | 8.685 | 22.499 | 304.2 | 6.837 | -61 | 86.2822 | [13 empty] | 99 | 277 | 60 | 276.96 | 60.97 | 8.183 | 0.4847 | 30.421 | 22.516 | 304.4 | 6.848 | -60.9744 | 83.6857
94 | 120 | 60 | 119.86 | 127.86 | 14.678 | 0.9575 | 5.404 | 44.725 | 288.74 | 12.903 | -62.9821 | 87.9071 | [13 empty] | 94 | 277 | 60 | 276.94 | 80.64 | 14.856 | 0.6651 | 20.293 | 44.69 | 289.17 | 12.912 | -62.9269 | 86.9144 | 94 | 120 | 60 | 119.9 | 72.31 | 7.524 | 0.8677 | 9.139 | 22.452 | 289.23 | 6.487 | -62.9192 | 86.2174 | [13 empty] | 94 | 277 | 60 | 276.96 | 59.85 | 7.788 | 0.4699 | 32.533 | 22.468 | 289.45 | 6.497 | -62.891 | 83.4232
89 | 120 | 60 | 119.87 | 121.95 | 13.938 | 0.9537 | 4.479 | 44.619 | 274.3 | 12.227 | -64.8333 | 87.7242 | [13 empty] | 89 | 277 | 60 | 276.94 | 78.41 | 14.084 | 0.6486 | 22.215 | 44.581 | 274.23 | 12.215 | -64.8423 | 86.7296 | 89 | 120 | 60 | 119.91 | 69.41 | 7.126 | 0.8562 | 9.565 | 22.404 | 274.25 | 6.138 | -64.8397 | 86.1353 | [13 empty] | 89 | 277 | 60 | 276.96 | 58.75 | 7.397 | 0.4546 | 32.794 | 22.419 | 274.51 | 6.149 | -64.8064 | 83.1283
84 | 120 | 60 | 119.87 | 115.28 | 13.116 | 0.95 | 4.414 | 44.504 | 258.86 | 11.509 | -66.8128 | 87.7478 | [13 empty] | 84 | 277 | 60 | 276.94 | 76.15 | 13.318 | 0.6316 | 22.955 | 44.471 | 259.24 | 11.518 | -66.7641 | 86.4845 | 84 | 120 | 60 | 119.91 | 66.6 | 6.731 | 0.843 | 12.156 | 22.354 | 259.16 | 5.787 | -66.7744 | 85.9753 | [13 empty] | 84 | 277 | 60 | 276.96 | 57.62 | 6.997 | 0.4384 | 33.801 | 22.369 | 259.45 | 5.798 | -66.7372 | 82.8641
79 | 120 | 60 | 119.88 | 109.07 | 12.345 | 0.9442 | 4.827 | 44.391 | 243.83 | 10.812 | -68.7397 | 87.582 | [13 empty] | 79 | 277 | 60 | 276.95 | 73.93 | 12.554 | 0.6131 | 22.678 | 44.358 | 244.23 | 10.824 | -68.6885 | 86.2195 | 79 | 120 | 60 | 119.91 | 63.74 | 6.334 | 0.8288 | 13.217 | 22.303 | 244.11 | 5.438 | -68.7038 | 85.8541 | [13 empty] | 79 | 277 | 60 | 276.96 | 56.6 | 6.611 | 0.4217 | 32.963 | 22.319 | 244.42 | 5.45 | -68.6641 | 82.4384
74 | 120 | 60 | 119.88 | 103.23 | 11.598 | 0.9372 | 6.634 | 44.276 | 229.03 | 10.131 | -70.6372 | 87.3513 | [13 empty] | 74 | 277 | 60 | 276.95 | 71.75 | 11.782 | 0.593 | 24.639 | 44.243 | 229.24 | 10.133 | -70.6103 | 86.0041 | 74 | 120 | 60 | 119.91 | 61 | 5.94 | 0.812 | 14.276 | 22.251 | 228.99 | 5.09 | -70.6423 | 85.6902 | [13 empty] | 74 | 277 | 60 | 276.96 | 55.6 | 6.213 | 0.4034 | 33.984 | 22.267 | 229.41 | 5.104 | -70.5885 | 82.1503
69 | 120 | 60 | 119.88 | 96.88 | 10.812 | 0.9306 | 5.239 | 44.154 | 213.74 | 9.428 | -72.5974 | 87.1994 | [13 empty] | 69 | 277 | 60 | 276.95 | 69.54 | 11.026 | 0.5725 | 25.615 | 44.124 | 214.25 | 9.446 | -72.5321 | 85.6702 | 69 | 120 | 60 | 119.91 | 58.33 | 5.547 | 0.793 | 12.699 | 22.198 | 213.97 | 4.744 | -72.5679 | 85.5237 | [13 empty] | 69 | 277 | 60 | 276.96 | 54.74 | 5.828 | 0.3844 | 36.709 | 22.214 | 214.41 | 4.759 | -72.5115 | 81.6575
64 | 120 | 60 | 119.89 | 90.95 | 10.041 | 0.9209 | 7.476 | 44.033 | 198.8 | 8.744 | -74.5128 | 87.083 | [13 empty] | 64 | 277 | 60 | 276.95 | 67.36 | 10.273 | 0.5507 | 27.106 | 44.003 | 199.23 | 8.759 | -74.4577 | 85.2623 | 64 | 120 | 60 | 119.92 | 55.69 | 5.158 | 0.7723 | 16.301 | 22.144 | 198.94 | 4.4 | -74.4949 | 85.3044 | [13 empty] | 64 | 277 | 60 | 276.96 | 53.8 | 5.438 | 0.365 | 36.852 | 22.158 | 199.35 | 4.413 | -74.4423 | 81.1512
59 | 120 | 60 | 119.89 | 85.19 | 9.297 | 0.9098 | 6.134 | 43.907 | 183.82 | 8.063 | -76.4333 | 86.7269 | [13 empty] | 59 | 277 | 60 | 276.95 | 65.19 | 9.52 | 0.5273 | 27.584 | 43.877 | 184.28 | 8.078 | -76.3744 | 84.8529 | 59 | 120 | 60 | 119.92 | 53.18 | 4.77 | 0.7481 | 14.897 | 22.087 | 183.92 | 4.057 | -76.4205 | 85.0524 | [13 empty] | 59 | 277 | 60 | 276.96 | 52.75 | 5.056 | 0.3461 | 37.225 | 22.102 | 184.44 | 4.073 | -76.3538 | 80.5578
54 | 120 | 60 | 119.9 | 79.29 | 8.531 | 0.8975 | 6.781 | 43.775 | 168.74 | 7.378 | -78.3667 | 86.4846 | [13 empty] | 54 | 277 | 60 | 276.95 | 63.03 | 8.772 | 0.5026 | 27.975 | 43.746 | 169.28 | 7.399 | -78.2974 | 84.3479 | 54 | 120 | 60 | 119.92 | 50.72 | 4.384 | 0.7207 | 18.058 | 22.028 | 168.93 | 3.716 | -78.3423 | 84.7628 | [13 empty] | 54 | 277 | 60 | 276.96 | 51.31 | 4.677 | 0.3291 | 37.434 | 22.045 | 169.83 | 3.741 | -78.2269 | 79.9872
49 | 120 | 60 | 119.91 | 134.53 | 7.179 | 0.445 | 92.539 | 43.518 | 134.09 | 5.835 | -82.809 | 81.2787 | [13 empty] | 49 | 277 | 60 | 276.96 | 77.06 | 7.289 | 0.3418 | 41.772 | 43.491 | 134.63 | 5.855 | -82.7397 | 80.3265 | 49 | 120 | 60 | 119.92 | 84.92 | 4.095 | 0.4013 | 79.921 | 21.959 | 152.16 | 3.341 | -80.4923 | 81.5873 | [13 empty] | 49 | 277 | 60 | 276.97 | 52.81 | 4.326 | 0.2957 | 38.851 | 21.98 | 154.37 | 3.393 | -80.209 | 78.4327
44 | 120 | 60 | 119.91 | 122.42 | 6.507 | 0.4429 | 87.728 | 43.389 | 121.85 | 5.286 | -84.3782 | 81.2356 | [13 empty] | 44 | 277 | 60 | 276.96 | 70.61 | 6.569 | 0.336 | 40.373 | 43.35 | 121.18 | 5.252 | -84.4641 | 79.9513 | 44 | 120 | 60 | 119.92 | 78.51 | 3.698 | 0.3926 | 78.15 | 21.962 | 137.13 | 3.011 | -82.4192 | 81.4224 | [13 empty] | 44 | 277 | 60 | 276.97 | 49.8 | 3.882 | 0.2815 | 38.134 | 21.972 | 136.76 | 3.0046 | -82.4667 | 77.3982
39 | 120 | 60 | 119.91 | 111.76 | 5.772 | 0.4314 | 88.209 | 43.239 | 108.19 | 4.677 | -86.1295 | 81.0291 | [13 empty] | 39 | 277 | 60 | 276.96 | 64.77 | 5.903 | 0.329 | 40.197 | 43.21 | 108.42 | 4.685 | -86.1 | 79.3664 | 39 | 120 | 60 | 119.93 | 72.99 | 3.287 | 0.3769 | 72.455 | 21.884 | 121.74 | 2.664 | -84.3923 | 81.0465 | [13 empty] | 39 | 277 | 60 | 276.97 | 47.74 | 3.511 | 0.2655 | 35.735 | 21.898 | 122.42 | 2.6804 | -84.3051 | 76.3429
34 | 120 | 60 | 119.92 | 101.51 | 5.111 | 0.4205 | 84.117 | 43.094 | 95.88 | 4.131 | -87.7077 | 80.8257 | [13 empty] | 34 | 277 | 60 | 276.96 | 58.86 | 5.208 | 0.3197 | 40.712 | 43.053 | 95.05 | 4.092 | -87.8141 | 78.5714 | 34 | 120 | 60 | 119.93 | 66.17 | 2.91 | 0.367 | 70.021 | 21.806 | 107.61 | 2.346 | -86.2038 | 80.6186 | [13 empty] | 34 | 277 | 60 | 276.97 | 45.51 | 3.112 | 0.2469 | 37.306 | 21.816 | 107.17 | 2.3378 | -86.2603 | 75.1221
29 | 120 | 60 | 119.92 | 89.32 | 4.398 | 0.4105 | 80.05 | 42.927 | 82.53 | 3.543 | -89.4192 | 80.5593 | [13 empty] | 29 | 277 | 60 | 276.97 | 54.28 | 4.565 | 0.3037 | 38.175 | 42.899 | 82.71 | 3.548 | -89.3962 | 77.7218 | 29 | 120 | 60 | 119.93 | 59.08 | 2.504 | 0.3535 | 65.747 | 21.718 | 92.43 | 2.007 | -88.15 | 80.1518 | [13 empty] | 29 | 277 | 60 | 276.97 | 43.25 | 2.724 | 0.2273 | 33.12 | 21.729 | 92.27 | 2.0046 | -88.1705 | 73.5903
24 | 120 | 60 | 119.92 | 80.23 | 3.72 | 0.3866 | 79.311 | 42.751 | 69.63 | 2.977 | -91.0731 | 80.0269 | [13 empty] | 24 | 277 | 60 | 276.97 | 49.82 | 3.901 | 0.2827 | 38.281 | 42.721 | 69.61 | 2.973 | -91.0756 | 76.2112 | 24 | 120 | 60 | 119.93 | 54.52 | 2.156 | 0.3298 | 63.753 | 21.629 | 78.39 | 1.695 | -89.95 | 78.6178 | [13 empty] | 24 | 277 | 60 | 276.97 | 41.54 | 2.37 | 0.2059 | 33.586 | 21.642 | 78.66 | 1.7022 | -89.9154 | 71.8228
19 | 120 | 60 | 119.93 | 67.83 | 3.036 | 0.3727 | 71.233 | 42.556 | 56.63 | 2.4096 | -92.7397 | 79.3676 | [13 empty] | 19 | 277 | 60 | 276.97 | 46.2 | 3.237 | 0.253 | 34.747 | 42.523 | 56.47 | 2.401 | -92.7603 | 74.1736 | 19 | 120 | 60 | 119.94 | 46.53 | 1.733 | 0.3108 | 54.092 | 21.513 | 62.43 | 1.343 | -91.9962 | 77.4957 | [13 empty] | 19 | 277 | 60 | 276.97 | 39.6 | 1.895 | 0.1727 | 28.242 | 21.525 | 62.24 | 1.3395 | -92.0205 | 70.686
14 | 120 | 60 | 119.93 | 56.33 | 2.31 | 0.3419 | 61.765 | 42.298 | 41.97 | 1.7754 | -94.6192 | 76.8571 | [13 empty] | 14 | 277 | 60 | 276.97 | 41.99 | 2.47 | 0.2123 | 32.322 | 42.248 | 41.08 | 1.7356 | -94.7333 | 70.2672 | 14 | 120 | 60 | 119.94 | 38.32 | 1.341 | 0.2916 | 53.864 | 21.388 | 47.35 | 1.0127 | -93.9295 | 75.5183 | [13 empty] | 14 | 277 | 60 | 276.97 | 38.01 | 1.463 | 0.1389 | 29.086 | 21.398 | 47.08 | 1.0073 | -93.9641 | 68.8517
9 | 120 | 60 | 119.93 | 43.57 | 1.607 | 0.3076 | 51.848 | 42 | 28.594 | 1.2008 | -96.3341 | 74.7231 | [13 empty] | 9 | 277 | 60 | 276.97 | 39 | 1.747 | 0.1617 | 30.495 | 41.963 | 28.403 | 1.1918 | -96.3586 | 68.2198 | 9 | 120 | 60 | 119.94 | 31.83 | 0.948 | 0.2485 | 44.391 | 21.23 | 32.21 | 0.6838 | -95.8705 | 72.1308 | [13 empty] | 9 | 277 | 60 | 276.97 | 36.63 | 1.044 | 0.1029 | 19.308 | 21.242 | 32.24 | 0.6847 | -95.8667 | 65.5843
4 | 120 | 60 | 119.94 | 31.47 | 0.924 | 0.2449 | 44.014 | 41.574 | 15.372 | 0.6391 | -98.0292 | 69.1667 | [13 empty] | 4 | 277 | 60 | 276.97 | 36.43 | 0.989 | 0.098 | 19.374 | 41.528 | 15.014 | 0.6234 | -98.0751 | 63.0334 | 4 | 120 | 60 | 119.94 | 30.6 | 0.849 | 0.2312 | 43.85 | 21.182 | 28.341 | 0.6003 | -96.3665 | 70.7067 | [13 empty] | 4 | 277 | 60 | 276.98 | 36.29 | 0.929 | 0.0924 | 24.243 | 21.192 | 28.23 | 0.5982 | -96.3808 | 64.3918
0 | 120 | 60 | 119.94 | 25.199 | 0.074 | 0.0244 | 35.626 | 37.648 | 0.0574 | 0.00197 | -99.9926 | 2.6622 | [13 empty] | 0 | 277 | 60 | 276.97 | 34.72 | 0.243 | 0.0252 | 6.915 | 37.588 | 0.0577 | 0.00197 | -99.9926 | 0.8107 | 0 | 120 | 60 | 119.95 | 25.184 | 0.0702 | 0.0233 | 34.656 | 18.629 | 0.0381 | 0.00061 | -99.9951 | 0.86895 | [13 empty] | 0 | 277 | 60 | 276.98 | 34.76 | 0.244 | 0.0254 | 8.544 | 18.641 | 0.0375 | 0.00062 | -99.9952 | 0.2541

## I2C Dimming (Logarithmic)
Logarithmic I2C Dimming
DER-925 Unit 9
48V LED, 120 VAC | [12 empty] | 46V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
254 | 120 | 60 | 119.89 | 347.58 | 41.31 | 0.9915 | 4.329 | 47.649 | 768.9 | 36.607 | -1.4231 | 88.6153 | [13 empty] | 254 | 277 | 60 | 276.87 | 165.23 | 41.257 | 0.9019 | 9.487 | 47.717 | 771.8 | 36.793 | -1.0513 | 89.18 | 254 | 120 | 60 | 119.83 | 180.77 | 21.089 | 0.9736 | 6.838 | 23.803 | 770.1 | 18.313 | -1.2692 | 86.8367 | [13 empty] | 254 | 277 | 60 | 276.92 | 100.86 | 21.356 | 0.7646 | 16.794 | 23.843 | 771.1 | 18.365 | -1.141 | 85.9946
251 | 120 | 60 | 119.89 | 318.26 | 37.825 | 0.9913 | 3.935 | 47.335 | 709.6 | 33.561 | -9.0256 | 88.727 | [13 empty] | 251 | 277 | 60 | 276.88 | 153.68 | 37.848 | 0.8896 | 10.194 | 47.401 | 712.3 | 33.73 | -8.6795 | 89.1196 | 251 | 120 | 60 | 119.84 | 166.07 | 19.34 | 0.9718 | 5.362 | 23.662 | 711.1 | 16.81 | -8.8333 | 86.9183 | [13 empty] | 251 | 277 | 60 | 276.92 | 95.32 | 19.615 | 0.7431 | 18.013 | 23.7 | 712 | 16.855 | -8.7179 | 85.9291
248 | 120 | 60 | 119.9 | 292.44 | 34.677 | 0.989 | 4.107 | 47.033 | 654.3 | 30.745 | -16.1154 | 88.6611 | [13 empty] | 248 | 277 | 60 | 276.89 | 143.18 | 34.718 | 0.8758 | 10.452 | 47.098 | 656.7 | 30.897 | -15.8077 | 88.9942 | 248 | 120 | 60 | 119.84 | 153 | 17.749 | 0.9679 | 5.596 | 23.53 | 656.5 | 15.431 | -15.8333 | 86.9401 | [13 empty] | 248 | 277 | 60 | 276.93 | 90.4 | 18.023 | 0.72 | 18.94 | 23.564 | 657.2 | 15.469 | -15.7436 | 85.8292
245 | 120 | 60 | 119.9 | 268.5 | 31.818 | 0.9884 | 3.957 | 46.757 | 604.5 | 28.236 | -22.5 | 88.7422 | [13 empty] | 245 | 277 | 60 | 276.89 | 133.74 | 31.887 | 0.8611 | 11.549 | 46.815 | 606.2 | 28.352 | -22.2821 | 88.914 | 245 | 120 | 60 | 119.85 | 141.24 | 16.305 | 0.9632 | 6.332 | 23.405 | 606.3 | 14.173 | -22.2692 | 86.9243 | [13 empty] | 245 | 277 | 60 | 276.93 | 85.93 | 16.581 | 0.6968 | 20.127 | 23.437 | 606.9 | 14.208 | -22.1923 | 85.6884
242 | 120 | 60 | 119.9 | 247.13 | 29.234 | 0.9866 | 4.024 | 46.499 | 558.1 | 25.927 | -28.4487 | 88.6878 | [13 empty] | 242 | 277 | 60 | 276.9 | 125.4 | 29.327 | 0.8446 | 12.266 | 46.547 | 559.8 | 26.031 | -28.2308 | 88.7612 | 242 | 120 | 60 | 119.86 | 130.6 | 14.985 | 0.9573 | 6.605 | 23.287 | 559.9 | 13.025 | -28.2179 | 86.9203 | [13 empty] | 242 | 277 | 60 | 276.94 | 81.93 | 15.262 | 0.6727 | 21.331 | 23.317 | 560.5 | 13.054 | -28.141 | 85.5327
239 | 120 | 60 | 119.91 | 227.25 | 26.814 | 0.9842 | 3.898 | 46.239 | 514.4 | 23.761 | -34.0513 | 88.6142 | [13 empty] | 239 | 277 | 60 | 276.9 | 117.78 | 26.97 | 0.8269 | 13.281 | 46.293 | 516.7 | 23.897 | -33.7564 | 88.6059 | 239 | 120 | 60 | 119.87 | 120.83 | 13.78 | 0.9514 | 6.421 | 23.175 | 517 | 11.969 | -33.7179 | 86.8578 | [13 empty] | 239 | 277 | 60 | 276.94 | 78.24 | 14.047 | 0.6483 | 22.365 | 23.204 | 517.4 | 11.994 | -33.6667 | 85.3848
236 | 120 | 60 | 119.91 | 209.37 | 24.667 | 0.9825 | 4.235 | 46 | 475.5 | 21.851 | -39.0385 | 88.5839 | [13 empty] | 236 | 277 | 60 | 276.91 | 110.91 | 24.814 | 0.808 | 14.396 | 46.051 | 476.8 | 21.935 | -38.8718 | 88.3977 | 236 | 120 | 60 | 119.87 | 111.93 | 12.662 | 0.9438 | 7.269 | 23.067 | 477.2 | 10.995 | -38.8205 | 86.8346 | [13 empty] | 236 | 277 | 60 | 276.94 | 74.92 | 12.937 | 0.6236 | 23.569 | 23.096 | 477.5 | 11.017 | -38.7821 | 85.1588
233 | 120 | 60 | 119.91 | 192.84 | 22.652 | 0.9796 | 4.453 | 45.771 | 438.6 | 20.052 | -43.7692 | 88.522 | [13 empty] | 233 | 277 | 60 | 276.91 | 104.74 | 22.846 | 0.7877 | 15.181 | 45.823 | 440.2 | 20.15 | -43.5641 | 88.1992 | 233 | 120 | 60 | 119.88 | 103.82 | 11.646 | 0.9358 | 7.477 | 22.967 | 440.5 | 10.104 | -43.5256 | 86.7594 | [13 empty] | 233 | 277 | 60 | 276.94 | 71.82 | 11.912 | 0.5989 | 24.667 | 22.994 | 440.5 | 10.117 | -43.5256 | 84.9312
230 | 120 | 60 | 119.91 | 178.22 | 20.863 | 0.9764 | 4.912 | 45.56 | 405.4 | 18.449 | -48.0256 | 88.4293 | [13 empty] | 230 | 277 | 60 | 276.92 | 99.12 | 21.022 | 0.766 | 16.396 | 45.606 | 406.2 | 18.507 | -47.9231 | 88.0363 | 230 | 120 | 60 | 119.88 | 96.4 | 10.697 | 0.9256 | 7.739 | 22.871 | 406.1 | 9.277 | -47.9359 | 86.7253 | [13 empty] | 230 | 277 | 60 | 276.95 | 69.07 | 10.972 | 0.5736 | 26.032 | 22.897 | 406.5 | 9.297 | -47.8846 | 84.7339
227 | 120 | 60 | 119.92 | 164.57 | 19.212 | 0.9737 | 4.908 | 45.357 | 374.3 | 16.962 | -52.0128 | 88.2886 | [13 empty] | 227 | 277 | 60 | 276.92 | 94.11 | 19.387 | 0.7438 | 17.711 | 45.402 | 375.1 | 17.014 | -51.9103 | 87.7598 | 227 | 120 | 60 | 119.89 | 89.91 | 9.858 | 0.9146 | 8.621 | 22.782 | 375.1 | 8.536 | -51.9103 | 86.5896 | [13 empty] | 227 | 277 | 60 | 276.95 | 66.56 | 10.125 | 0.5493 | 27.244 | 22.806 | 375.4 | 8.551 | -51.8718 | 84.4543
224 | 120 | 60 | 119.92 | 152.21 | 17.67 | 0.968 | 5.284 | 45.164 | 345.6 | 15.592 | -55.6923 | 88.24 | [13 empty] | 224 | 277 | 60 | 276.92 | 89.54 | 17.865 | 0.7204 | 18.592 | 45.208 | 346.3 | 15.642 | -55.6026 | 87.5567 | 224 | 120 | 60 | 119.89 | 83.88 | 9.077 | 0.9026 | 9.772 | 22.697 | 346.3 | 7.851 | -55.6026 | 86.4933 | [13 empty] | 224 | 277 | 60 | 276.95 | 64.3 | 9.344 | 0.5248 | 28.465 | 22.72 | 346.6 | 7.868 | -55.5641 | 84.2038
221 | 120 | 60 | 119.85 | 140.84 | 16.295 | 0.9653 | 3.83 | 44.983 | 319.2 | 14.347 | -59.0769 | 88.0454 | [13 empty] | 221 | 277 | 60 | 276.93 | 85.43 | 16.48 | 0.6966 | 19.787 | 45.024 | 319.7 | 14.383 | -59.0128 | 87.2755 | 221 | 120 | 60 | 119.9 | 78.51 | 8.361 | 0.8883 | 10.398 | 22.616 | 319.7 | 7.224 | -59.0128 | 86.4011 | [13 empty] | 221 | 277 | 60 | 276.95 | 62.19 | 8.628 | 0.5009 | 29.562 | 22.638 | 320 | 7.237 | -58.9744 | 83.8781
218 | 120 | 60 | 119.86 | 130.16 | 14.971 | 0.9595 | 4.099 | 44.805 | 294.18 | 13.167 | -62.2846 | 87.95 | [13 empty] | 218 | 277 | 60 | 276.93 | 81.7 | 15.21 | 0.6723 | 21.085 | 44.849 | 295.15 | 13.226 | -62.1603 | 86.956 | 218 | 120 | 60 | 119.9 | 73.6 | 7.702 | 0.8727 | 10.839 | 22.537 | 295.11 | 6.644 | -62.1654 | 86.2633 | [13 empty] | 218 | 277 | 60 | 276.95 | 60.32 | 7.972 | 0.4772 | 30.581 | 22.56 | 295.39 | 6.657 | -62.1295 | 83.5048
215 | 120 | 60 | 119.86 | 121.09 | 13.839 | 0.9533 | 4.369 | 44.642 | 272.06 | 12.135 | -65.1205 | 87.687 | [13 empty] | 215 | 277 | 60 | 276.93 | 78.26 | 14.032 | 0.6474 | 22.123 | 44.68 | 272.44 | 12.162 | -65.0718 | 86.6733 | 215 | 120 | 60 | 119.9 | 69.18 | 7.099 | 0.8558 | 11.207 | 22.462 | 272.4 | 6.112 | -65.0769 | 86.0966 | [13 empty] | 215 | 277 | 60 | 276.96 | 58.63 | 7.375 | 0.4541 | 31.556 | 22.485 | 272.71 | 6.126 | -65.0372 | 83.0644
212 | 120 | 60 | 119.87 | 111.87 | 12.704 | 0.9475 | 4.669 | 44.481 | 250.59 | 11.134 | -67.8731 | 87.6417 | [13 empty] | 212 | 277 | 60 | 276.93 | 75.12 | 12.96 | 0.623 | 22.473 | 44.523 | 251.61 | 11.193 | -67.7423 | 86.3657 | 212 | 120 | 60 | 119.91 | 65.23 | 6.547 | 0.837 | 10.488 | 22.391 | 251.42 | 5.623 | -67.7667 | 85.8867 | [13 empty] | 212 | 277 | 60 | 276.95 | 57.12 | 6.824 | 0.4314 | 32.524 | 22.413 | 251.83 | 5.639 | -67.7141 | 82.6348
209 | 120 | 60 | 119.88 | 104.3 | 11.732 | 0.9384 | 5.152 | 44.336 | 231.71 | 10.264 | -70.2936 | 87.4872 | [13 empty] | 209 | 277 | 60 | 276.94 | 72.29 | 11.973 | 0.598 | 23.429 | 44.374 | 232.3 | 10.299 | -70.2179 | 86.0185 | 209 | 120 | 60 | 119.91 | 61.6 | 6.034 | 0.8168 | 11.348 | 22.323 | 231.96 | 5.172 | -70.2615 | 85.7143 | [13 empty] | 209 | 277 | 60 | 276.96 | 55.79 | 6.312 | 0.4086 | 33.43 | 22.346 | 232.42 | 5.189 | -70.2026 | 82.2085
206 | 120 | 60 | 119.88 | 96.97 | 10.821 | 0.9308 | 5.239 | 44.192 | 213.59 | 9.428 | -72.6167 | 87.1269 | [13 empty] | 206 | 277 | 60 | 276.94 | 69.65 | 11.066 | 0.5737 | 24.945 | 44.232 | 214.43 | 9.477 | -72.509 | 85.6407 | 206 | 120 | 60 | 119.91 | 58.42 | 5.567 | 0.7946 | 14.962 | 22.259 | 214.04 | 4.759 | -72.559 | 85.4859 | [13 empty] | 206 | 277 | 60 | 276.96 | 54.68 | 5.849 | 0.3863 | 34.07 | 22.282 | 214.57 | 4.777 | -72.491 | 81.6721
203 | 120 | 60 | 119.89 | 90.65 | 10.003 | 0.9205 | 5.759 | 44.06 | 197.54 | 8.694 | -74.6744 | 86.9139 | [13 empty] | 203 | 277 | 60 | 276.94 | 67.26 | 10.235 | 0.5495 | 25.882 | 44.097 | 198.06 | 8.726 | -74.6077 | 85.2565 | 203 | 120 | 60 | 119.91 | 55.52 | 5.139 | 0.7718 | 16.404 | 22.199 | 197.69 | 4.383 | -74.6551 | 85.289 | [13 empty] | 203 | 277 | 60 | 276.96 | 53.68 | 5.426 | 0.365 | 36.552 | 22.221 | 198.13 | 4.398 | -74.5987 | 81.0542
200 | 120 | 60 | 119.89 | 84.56 | 9.213 | 0.9087 | 6.166 | 43.93 | 182.12 | 7.991 | -76.6513 | 86.7361 | [13 empty] | 200 | 277 | 60 | 276.94 | 65.08 | 9.476 | 0.5258 | 27.017 | 43.968 | 182.89 | 8.035 | -76.5526 | 84.7932 | 200 | 120 | 60 | 119.92 | 52.96 | 4.744 | 0.747 | 16.705 | 22.141 | 182.5 | 4.036 | -76.6026 | 85.0759 | [13 empty] | 200 | 277 | 60 | 276.96 | 52.7 | 5.036 | 0.345 | 36.521 | 22.163 | 183.1 | 4.054 | -76.5256 | 80.5004
197 | 120 | 60 | 119.89 | 79.04 | 8.5 | 0.897 | 6.78 | 43.806 | 168.06 | 7.354 | -78.4538 | 86.5176 | [13 empty] | 197 | 277 | 60 | 276.94 | 63.03 | 8.773 | 0.5026 | 27.855 | 43.844 | 168.84 | 7.396 | -78.3538 | 84.3041 | 197 | 120 | 60 | 119.92 | 50.64 | 4.38 | 0.7212 | 18.158 | 22.085 | 168.43 | 3.715 | -78.4064 | 84.8174 | [13 empty] | 197 | 277 | 60 | 276.96 | 51.34 | 4.679 | 0.329 | 36.209 | 22.108 | 169.43 | 3.743 | -78.2782 | 79.9957
194 | 120 | 60 | 119.93 | 138.79 | 7.312 | 0.4391 | 97.401 | 43.579 | 136.37 | 5.942 | -82.5167 | 81.2637 | [13 empty] | 194 | 277 | 60 | 276.95 | 79.55 | 7.394 | 0.3358 | 42.52 | 43.607 | 136.21 | 5.939 | -82.5372 | 80.3219 | 194 | 120 | 60 | 119.92 | 87.59 | 4.29 | 0.4082 | 78.489 | 22.048 | 158.91 | 3.503 | -79.6269 | 81.655 | [13 empty] | 194 | 277 | 60 | 276.96 | 53.57 | 4.443 | 0.2995 | 39.628 | 22.061 | 157.91 | 3.483 | -79.7551 | 78.393
191 | 120 | 60 | 119.9 | 124.9 | 6.703 | 0.4476 | 91.405 | 43.465 | 125.37 | 5.449 | -83.9269 | 81.292 | [13 empty] | 191 | 277 | 60 | 276.95 | 74.47 | 6.836 | 0.3313 | 41.598 | 43.499 | 125.78 | 5.471 | -83.8744 | 80.0322 | 191 | 120 | 60 | 119.92 | 81.56 | 3.854 | 0.3938 | 75.61 | 22.047 | 142.36 | 3.138 | -81.7487 | 81.4219 | [13 empty] | 191 | 277 | 60 | 276.96 | 50.68 | 4.02 | 0.2864 | 40.029 | 22.061 | 141.45 | 3.1203 | -81.8654 | 77.6194
188 | 120 | 60 | 119.91 | 118.14 | 6.218 | 0.4396 | 87.603 | 43.368 | 116.34 | 5.045 | -85.0846 | 81.1354 | [13 empty] | 188 | 277 | 60 | 276.95 | 68.75 | 6.317 | 0.3318 | 40.967 | 43.393 | 115.92 | 5.029 | -85.1385 | 79.6106 | 188 | 120 | 60 | 119.92 | 76.11 | 3.541 | 0.3877 | 76.234 | 21.99 | 130.8 | 2.876 | -83.2308 | 81.22 | [13 empty] | 188 | 277 | 60 | 276.96 | 48.91 | 3.736 | 0.2757 | 38.457 | 22.006 | 130.47 | 2.8706 | -83.2731 | 76.8362
185 | 120 | 60 | 119.91 | 110.69 | 5.722 | 0.4314 | 88.273 | 43.266 | 107.1 | 4.633 | -86.2692 | 80.9682 | [13 empty] | 185 | 277 | 60 | 276.95 | 64.94 | 5.862 | 0.3261 | 39.473 | 43.296 | 107.28 | 4.644 | -86.2462 | 79.2221 | 185 | 120 | 60 | 119.92 | 71.66 | 3.253 | 0.3792 | 70.733 | 21.933 | 120.01 | 2.632 | -84.6141 | 80.9099 | [13 empty] | 185 | 277 | 60 | 276.96 | 47.48 | 3.464 | 0.2634 | 37.148 | 21.95 | 119.9 | 2.6314 | -84.6282 | 75.9642
182 | 120 | 60 | 119.91 | 103.76 | 5.289 | 0.4249 | 85.769 | 43.173 | 99.1 | 4.278 | -87.2949 | 80.8849 | [13 empty] | 182 | 277 | 60 | 276.95 | 60.92 | 5.44 | 0.3225 | 39.701 | 43.201 | 99.14 | 4.283 | -87.2897 | 78.7316 | 182 | 120 | 60 | 119.92 | 67.47 | 3.023 | 0.3732 | 68.04 | 21.888 | 111.53 | 2.441 | -85.7013 | 80.7476 | [13 empty] | 182 | 277 | 60 | 276.96 | 46.19 | 3.229 | 0.2524 | 37.044 | 21.901 | 110.97 | 2.43 | -85.7731 | 75.2555
179 | 120 | 60 | 119.91 | 98.46 | 4.872 | 0.4123 | 85.927 | 43.079 | 91.29 | 3.932 | -88.2962 | 80.7061 | [13 empty] | 179 | 277 | 60 | 276.95 | 57.86 | 5.045 | 0.3147 | 41.082 | 43.109 | 91.57 | 3.947 | -88.2603 | 78.2359 | 179 | 120 | 60 | 119.93 | 64.47 | 2.789 | 0.3612 | 66.923 | 21.838 | 102.65 | 2.241 | -86.8397 | 80.3514 | [13 empty] | 179 | 277 | 60 | 276.96 | 44.86 | 3.009 | 0.2422 | 35.884 | 21.854 | 102.66 | 2.2433 | -86.8385 | 74.553
176 | 120 | 60 | 119.92 | 90.27 | 4.5 | 0.4152 | 79.289 | 42.992 | 84.34 | 3.626 | -89.1872 | 80.5778 | [13 empty] | 176 | 277 | 60 | 276.95 | 55.02 | 4.667 | 0.3063 | 40.291 | 43.018 | 84.34 | 3.628 | -89.1872 | 77.7373 | 176 | 120 | 60 | 119.93 | 60.29 | 2.575 | 0.3562 | 65.992 | 21.791 | 94.64 | 2.062 | -87.8667 | 80.0777 | [13 empty] | 176 | 277 | 60 | 276.96 | 43.64 | 2.799 | 0.2316 | 36.418 | 21.807 | 94.58 | 2.0623 | -87.8744 | 73.6799
173 | 120 | 60 | 119.92 | 87.07 | 4.181 | 0.4006 | 77.679 | 42.914 | 78.32 | 3.361 | -89.959 | 80.3875 | [13 empty] | 173 | 277 | 60 | 276.96 | 52.93 | 4.348 | 0.2965 | 39.646 | 42.938 | 78.19 | 3.357 | -89.9756 | 77.2079 | 173 | 120 | 60 | 119.93 | 57.56 | 2.371 | 0.3436 | 62.651 | 21.739 | 86.15 | 1.873 | -88.9551 | 78.9962 | [13 empty] | 173 | 277 | 60 | 276.96 | 42.77 | 2.629 | 0.2219 | 35.464 | 21.762 | 87.36 | 1.901 | -88.8 | 72.3089
170 | 120 | 60 | 119.92 | 82.72 | 3.885 | 0.3914 | 80.173 | 42.838 | 72.67 | 3.112 | -90.6833 | 80.103 | [13 empty] | 170 | 277 | 60 | 276.96 | 50.94 | 4.057 | 0.2876 | 38.835 | 42.86 | 72.41 | 3.103 | -90.7167 | 76.4851 | 170 | 120 | 60 | 119.93 | 54.94 | 2.19 | 0.3327 | 60.1 | 21.696 | 79.36 | 1.722 | -89.8256 | 78.6301 | [13 empty] | 170 | 277 | 60 | 276.96 | 41.96 | 2.453 | 0.2111 | 35.211 | 21.721 | 80.96 | 1.7585 | -89.6205 | 71.6877
167 | 120 | 60 | 119.92 | 77.46 | 3.579 | 0.3853 | 79.364 | 42.756 | 66.91 | 2.86 | -91.4218 | 79.9106 | [13 empty] | 167 | 277 | 60 | 276.96 | 49.2 | 3.786 | 0.2778 | 37.25 | 42.783 | 66.99 | 2.866 | -91.4115 | 75.6999 | 167 | 120 | 60 | 119.93 | 53.78 | 2.064 | 0.3202 | 59.128 | 21.665 | 74.74 | 1.619 | -90.4179 | 78.4399 | [13 empty] | 167 | 277 | 60 | 276.97 | 41.11 | 2.261 | 0.1986 | 31.115 | 21.678 | 74.57 | 1.6165 | -90.4397 | 71.4949
164 | 120 | 60 | 119.92 | 73.18 | 3.304 | 0.3767 | 76.276 | 42.678 | 61.63 | 2.63 | -92.0987 | 79.6005 | [13 empty] | 164 | 277 | 60 | 276.96 | 47.85 | 3.52 | 0.2657 | 37.191 | 42.706 | 61.81 | 2.639 | -92.0756 | 74.9716 | 164 | 120 | 60 | 119.93 | 49.99 | 1.901 | 0.3172 | 56.033 | 21.622 | 68.5 | 1.481 | -91.2179 | 77.9064 | [13 empty] | 164 | 277 | 60 | 276.97 | 40.12 | 2.028 | 0.1825 | 29.483 | 21.62 | 66.47 | 1.4369 | -91.4782 | 70.8531
161 | 120 | 60 | 119.92 | 67.98 | 3.057 | 0.3753 | 70.174 | 42.606 | 56.98 | 2.4271 | -92.6949 | 79.3948 | [13 empty] | 161 | 277 | 60 | 276.96 | 46.38 | 3.268 | 0.2544 | 37.695 | 42.627 | 56.75 | 2.4188 | -92.7244 | 74.0147 | 161 | 120 | 60 | 119.93 | 46.85 | 1.737 | 0.309 | 54.428 | 21.574 | 62.23 | 1.343 | -92.0218 | 77.3172 | [13 empty] | 161 | 277 | 60 | 276.97 | 39.7 | 1.919 | 0.1745 | 28.078 | 21.592 | 62.74 | 1.3545 | -91.9564 | 70.5836
158 | 120 | 60 | 119.93 | 63.75 | 2.72 | 0.3557 | 72.865 | 42.484 | 49.62 | 2.1081 | -93.6385 | 77.5037 | [13 empty] | 158 | 277 | 60 | 276.96 | 44.81 | 3.008 | 0.2424 | 36.897 | 42.533 | 50.99 | 2.1688 | -93.4628 | 72.1011 | 158 | 120 | 60 | 119.93 | 44.17 | 1.626 | 0.307 | 53.475 | 21.542 | 58.1 | 1.2514 | -92.5513 | 76.9619 | [13 empty] | 158 | 277 | 60 | 276.97 | 39.2 | 1.788 | 0.1646 | 32.123 | 21.556 | 58.1 | 1.2523 | -92.5513 | 70.0391
155 | 120 | 60 | 119.93 | 58.73 | 2.482 | 0.3526 | 63.83 | 42.405 | 45.16 | 1.9151 | -94.2103 | 77.1595 | [13 empty] | 155 | 277 | 60 | 276.96 | 43.39 | 2.755 | 0.2293 | 36.639 | 42.446 | 46.03 | 1.9535 | -94.0987 | 70.9074 | 155 | 120 | 60 | 119.93 | 41.51 | 1.496 | 0.3005 | 50.374 | 21.5 | 53.08 | 1.1412 | -93.1949 | 76.2834 | [13 empty] | 155 | 277 | 60 | 276.97 | 38.64 | 1.638 | 0.153 | 29.824 | 21.514 | 53.03 | 1.1407 | -93.2013 | 69.6398
152 | 120 | 60 | 119.93 | 57.44 | 2.39 | 0.3467 | 63.899 | 42.375 | 43.46 | 1.8416 | -94.4282 | 77.0544 | [13 empty] | 152 | 277 | 60 | 276.96 | 42.49 | 2.582 | 0.2195 | 34.88 | 42.386 | 42.8 | 1.8141 | -94.5128 | 70.2595 | 152 | 120 | 60 | 119.93 | 39.23 | 1.387 | 0.2949 | 50.223 | 21.466 | 48.99 | 1.0514 | -93.7192 | 75.8039 | [13 empty] | 152 | 277 | 60 | 276.97 | 38.21 | 1.517 | 0.1433 | 28.827 | 21.476 | 48.74 | 1.0468 | -93.7513 | 69.0046
149 | 120 | 60 | 119.93 | 53.28 | 2.189 | 0.3434 | 58.464 | 42.299 | 39.57 | 1.6739 | -94.9269 | 76.4687 | [13 empty] | 149 | 277 | 60 | 276.96 | 41.55 | 2.371 | 0.206 | 33.917 | 42.315 | 39.16 | 1.6571 | -94.9795 | 69.8903 | 149 | 120 | 60 | 119.94 | 37.08 | 1.283 | 0.2885 | 51.012 | 21.43 | 45.06 | 0.9655 | -94.2231 | 75.2533 | [13 empty] | 149 | 277 | 60 | 276.97 | 37.83 | 1.41 | 0.1346 | 27.624 | 21.442 | 44.96 | 0.9639 | -94.2359 | 68.3617
146 | 120 | 60 | 119.93 | 51.2 | 2.011 | 0.3277 | 58.605 | 42.23 | 36.28 | 1.5322 | -95.3487 | 76.1909 | [13 empty] | 146 | 277 | 60 | 276.96 | 40.88 | 2.209 | 0.1951 | 33.065 | 42.256 | 36.35 | 1.5359 | -95.3397 | 69.5292 | 146 | 120 | 60 | 119.93 | 35.68 | 1.197 | 0.2796 | 50.752 | 21.397 | 41.66 | 0.8913 | -94.659 | 74.4612 | [13 empty] | 146 | 277 | 60 | 276.97 | 37.49 | 1.313 | 0.1264 | 22.679 | 21.409 | 41.55 | 0.8896 | -94.6731 | 67.7532
143 | 120 | 60 | 119.93 | 48.76 | 1.878 | 0.3215 | 55.756 | 42.174 | 33.71 | 1.4217 | -95.6782 | 75.7029 | [13 empty] | 143 | 277 | 60 | 276.96 | 40.29 | 2.072 | 0.1856 | 31.554 | 42.202 | 33.94 | 1.4322 | -95.6487 | 69.1216 | 143 | 120 | 60 | 119.94 | 34.11 | 1.103 | 0.2699 | 47.187 | 21.362 | 38.11 | 0.814 | -95.1141 | 73.7987 | [13 empty] | 143 | 277 | 60 | 276.97 | 37.15 | 1.213 | 0.1179 | 23.028 | 21.373 | 37.99 | 0.812 | -95.1295 | 66.9415
140 | 120 | 60 | 119.93 | 46.13 | 1.73 | 0.3128 | 55.086 | 42.11 | 30.89 | 1.3005 | -96.0397 | 75.1734 | [13 empty] | 140 | 277 | 60 | 276.96 | 39.69 | 1.915 | 0.1742 | 27.894 | 42.139 | 31.19 | 1.3143 | -96.0013 | 68.6319 | 140 | 120 | 60 | 119.94 | 33.09 | 1.034 | 0.2605 | 45.917 | 21.331 | 35.32 | 0.7534 | -95.4718 | 72.8627 | [13 empty] | 140 | 277 | 60 | 276.97 | 36.9 | 1.132 | 0.1108 | 20.854 | 21.344 | 35.34 | 0.7541 | -95.4692 | 66.6166
137 | 120 | 60 | 119.93 | 43.55 | 1.61 | 0.3083 | 51.53 | 42.054 | 28.608 | 1.2031 | -96.3323 | 74.7267 | [13 empty] | 137 | 277 | 60 | 276.96 | 39.07 | 1.76 | 0.1627 | 26.88 | 42.075 | 28.535 | 1.2006 | -96.3417 | 68.2159 | 137 | 120 | 60 | 119.94 | 31.97 | 0.959 | 0.25 | 44.767 | 21.299 | 32.46 | 0.6913 | -95.8385 | 72.0855 | [13 empty] | 137 | 277 | 60 | 276.97 | 36.65 | 1.054 | 0.1038 | 20.422 | 21.31 | 32.4 | 0.6905 | -95.8462 | 65.5123
134 | 120 | 60 | 119.93 | 41.42 | 1.501 | 0.3022 | 50.839 | 42 | 26.485 | 1.1123 | -96.6045 | 74.1039 | [13 empty] | 134 | 277 | 60 | 276.96 | 38.68 | 1.651 | 0.1541 | 26.647 | 42.026 | 26.637 | 1.1194 | -96.585 | 67.8013 | 134 | 120 | 60 | 119.94 | 31.14 | 0.893 | 0.2392 | 42.318 | 21.267 | 29.845 | 0.6347 | -96.1737 | 71.075 | [13 empty] | 134 | 277 | 60 | 276.97 | 36.43 | 0.974 | 0.0966 | 18.4 | 21.276 | 29.595 | 0.6296 | -96.2058 | 64.6407
131 | 120 | 60 | 119.93 | 39.1 | 1.39 | 0.2964 | 48.168 | 41.943 | 24.393 | 1.0231 | -96.8727 | 73.6043 | [13 empty] | 131 | 277 | 60 | 276.96 | 38.18 | 1.511 | 0.1429 | 25.266 | 41.959 | 24.189 | 1.0149 | -96.8988 | 67.1674 | 131 | 120 | 60 | 119.94 | 30.51 | 0.838 | 0.229 | 42.37 | 21.24 | 27.808 | 0.5906 | -96.4349 | 70.4773 | [13 empty] | 131 | 277 | 60 | 276.97 | 36.28 | 0.92 | 0.0916 | 18.685 | 21.252 | 27.714 | 0.5889 | -96.4469 | 64.0109
128 | 120 | 60 | 119.93 | 36.94 | 1.28 | 0.2887 | 47.124 | 41.882 | 22.289 | 0.9335 | -97.1424 | 72.9297 | [13 empty] | 128 | 277 | 60 | 276.96 | 37.78 | 1.401 | 0.1339 | 23.981 | 41.902 | 22.24 | 0.9318 | -97.1487 | 66.5096 | 128 | 120 | 60 | 119.94 | 30.5 | 0.837 | 0.2289 | 40.78 | 21.241 | 27.796 | 0.5904 | -96.4364 | 70.5376 | [13 empty] | 128 | 277 | 60 | 276.97 | 36.27 | 0.915 | 0.0911 | 18.602 | 21.252 | 27.699 | 0.5886 | -96.4488 | 64.3279
125 | 120 | 60 | 119.93 | 35.71 | 1.202 | 0.2805 | 46.397 | 41.835 | 20.756 | 0.8683 | -97.339 | 72.2379 | [13 empty] | 125 | 277 | 60 | 276.96 | 37.46 | 1.307 | 0.126 | 21.547 | 41.849 | 20.527 | 0.859 | -97.3683 | 65.723 | 125 | 120 | 60 | 119.94 | 30.6 | 0.838 | 0.2282 | 42.344 | 21.241 | 27.813 | 0.5907 | -96.4342 | 70.4893 | [13 empty] | 125 | 277 | 60 | 276.97 | 36.28 | 0.92 | 0.0915 | 18.859 | 21.252 | 27.718 | 0.589 | -96.4464 | 64.0217
122 | 120 | 60 | 119.94 | 33.92 | 1.095 | 0.2693 | 48.616 | 41.767 | 18.724 | 0.782 | -97.5995 | 71.4155 | [13 empty] | 122 | 277 | 60 | 276.96 | 37.14 | 1.213 | 0.1179 | 27.015 | 41.796 | 18.942 | 0.7917 | -97.5715 | 65.2679 | 122 | 120 | 60 | 119.94 | 30.52 | 0.838 | 0.2291 | 47.341 | 21.242 | 27.802 | 0.5905 | -96.4356 | 70.4654 | [13 empty] | 122 | 277 | 60 | 276.97 | 36.26 | 0.916 | 0.0912 | 17.708 | 21.252 | 27.683 | 0.5883 | -96.4509 | 64.2249
119 | 120 | 60 | 119.93 | 32.88 | 1.028 | 0.2607 | 44.759 | 41.719 | 17.358 | 0.7241 | -97.7746 | 70.4377 | [13 empty] | 119 | 277 | 60 | 276.96 | 36.85 | 1.118 | 0.1096 | 21.144 | 41.735 | 17.206 | 0.718 | -97.7941 | 64.2218 | 119 | 120 | 60 | 119.94 | 30.48 | 0.836 | 0.2287 | 42.374 | 21.242 | 27.803 | 0.5906 | -96.4355 | 70.6459 | [13 empty] | 119 | 277 | 60 | 276.97 | 36.25 | 0.917 | 0.0913 | 18.789 | 21.253 | 27.684 | 0.5883 | -96.4508 | 64.1549
116 | 120 | 60 | 119.93 | 31.91 | 0.952 | 0.2489 | 47.744 | 41.664 | 15.933 | 0.6638 | -97.9573 | 69.7269 | [13 empty] | 116 | 277 | 60 | 276.96 | 36.57 | 1.03 | 0.1017 | 23.467 | 41.677 | 15.716 | 0.6549 | -97.9851 | 63.5825 | 116 | 120 | 60 | 119.94 | 30.49 | 0.838 | 0.2292 | 48.9 | 21.242 | 27.792 | 0.5903 | -96.4369 | 70.4415 | [13 empty] | 116 | 277 | 60 | 276.97 | 36.26 | 0.92 | 0.0916 | 22.318 | 21.253 | 27.691 | 0.5885 | -96.4499 | 63.9674
113 | 120 | 60 | 119.94 | 31 | 0.886 | 0.2383 | 42.017 | 41.611 | 14.621 | 0.6084 | -98.1255 | 68.6682 | [13 empty] | 113 | 277 | 60 | 276.96 | 36.4 | 0.975 | 0.0967 | 18.616 | 41.634 | 14.639 | 0.6095 | -98.1232 | 62.5128 | 113 | 120 | 60 | 119.94 | 30.47 | 0.837 | 0.229 | 41.449 | 21.242 | 27.792 | 0.5903 | -96.4369 | 70.5257 | [13 empty] | 113 | 277 | 60 | 276.97 | 36.26 | 0.916 | 0.0912 | 18.899 | 21.253 | 27.685 | 0.5884 | -96.4506 | 64.2358
110 | 120 | 60 | 119.93 | 31.05 | 0.883 | 0.2373 | 44.194 | 41.579 | 13.897 | 0.5778 | -98.2183 | 65.436 | [13 empty] | 110 | 277 | 60 | 276.96 | 36.28 | 0.927 | 0.0923 | 17.926 | 41.56 | 13.048 | 0.5423 | -98.3272 | 58.5005 | 110 | 120 | 60 | 119.94 | 30.49 | 0.836 | 0.2286 | 41.852 | 21.242 | 27.79 | 0.5903 | -96.4372 | 70.61 | [13 empty] | 110 | 277 | 60 | 276.97 | 36.25 | 0.92 | 0.0916 | 23.473 | 21.254 | 27.684 | 0.5884 | -96.4508 | 63.9565
107 | 120 | 60 | 119.94 | 30.534 | 0.8406 | 0.2296 | 47.804 | 41.542 | 13.066 | 0.5428 | -98.3249 | 64.5729 | [13 empty] | 107 | 277 | 60 | 276.96 | 36.22 | 0.91 | 0.0908 | 24.241 | 41.551 | 12.819 | 0.5326 | -98.3565 | 58.5275 | 107 | 120 | 60 | 119.94 | 30.48 | 0.838 | 0.2291 | 48.031 | 21.243 | 27.787 | 0.5902 | -96.4376 | 70.4296 | [13 empty] | 107 | 277 | 60 | 276.97 | 36.23 | 0.915 | 0.0912 | 17.269 | 21.255 | 27.678 | 0.5882 | -96.4515 | 64.2842
104 | 120 | 60 | 119.93 | 29.258 | 0.7174 | 0.2045 | 38.256 | 41.412 | 10.562 | 0.4374 | -98.6459 | 60.9702 | [13 empty] | 104 | 277 | 60 | 276.96 | 36.01 | 0.831 | 0.0833 | 17.02 | 41.485 | 11.491 | 0.4767 | -98.5268 | 57.3646 | 104 | 120 | 60 | 119.94 | 30.5 | 0.838 | 0.2292 | 46.805 | 21.243 | 27.776 | 0.59 | -96.439 | 70.4057 | [13 empty] | 104 | 277 | 60 | 276.97 | 36.29 | 0.92 | 0.0915 | 24.4 | 21.255 | 27.707 | 0.5889 | -96.4478 | 64.0109
101 | 120 | 60 | 119.94 | 29.172 | 0.7046 | 0.2014 | 38.713 | 41.404 | 10.408 | 0.4309 | -98.6656 | 61.1553 | [13 empty] | 101 | 277 | 60 | 276.96 | 35.83 | 0.766 | 0.0772 | 17.336 | 41.427 | 10.448 | 0.4328 | -98.6605 | 56.5013 | 101 | 120 | 60 | 119.94 | 30.5 | 0.838 | 0.2292 | 43.534 | 21.244 | 27.767 | 0.5898 | -96.4401 | 70.3819 | [13 empty] | 101 | 277 | 60 | 276.97 | 36.26 | 0.916 | 0.0912 | 18.154 | 21.255 | 27.678 | 0.5883 | -96.4515 | 64.2249
98 | 120 | 60 | 119.94 | 28.698 | 0.6497 | 0.1888 | 38.922 | 41.342 | 9.362 | 0.387 | -98.7997 | 59.566 | [13 empty] | 98 | 277 | 60 | 276.97 | 35.63 | 0.684 | 0.0694 | 22.189 | 41.339 | 9.006 | 0.3723 | -98.8454 | 54.4298 | 98 | 120 | 60 | 119.94 | 30.5 | 0.838 | 0.2291 | 50.223 | 21.244 | 27.78 | 0.5901 | -96.4385 | 70.4177 | [13 empty] | 98 | 277 | 60 | 276.97 | 36.23 | 0.919 | 0.0916 | 18.633 | 21.255 | 27.669 | 0.588 | -96.4527 | 63.9826
95 | 120 | 60 | 119.94 | 28.354 | 0.6153 | 0.181 | 45.08 | 41.303 | 8.741 | 0.361 | -98.8794 | 58.6706 | [13 empty] | 95 | 277 | 60 | 276.96 | 35.58 | 0.661 | 0.0671 | 14.588 | 41.316 | 8.644 | 0.3571 | -98.8918 | 54.0242 | 95 | 120 | 60 | 119.94 | 30.48 | 0.837 | 0.229 | 45.93 | 21.245 | 27.771 | 0.5899 | -96.4396 | 70.4779 | [13 empty] | 95 | 277 | 60 | 276.97 | 36.27 | 0.92 | 0.0915 | 18.914 | 21.256 | 27.696 | 0.5886 | -96.4492 | 63.9783
92 | 120 | 60 | 119.94 | 27.826 | 0.5635 | 0.1688 | 36.772 | 41.236 | 7.797 | 0.3215 | -99.0004 | 57.0541 | [13 empty] | 92 | 277 | 60 | 276.96 | 35.42 | 0.601 | 0.0613 | 14.814 | 41.239 | 7.572 | 0.3123 | -99.0292 | 51.9634 | 92 | 120 | 60 | 119.94 | 30.5 | 0.836 | 0.2286 | 42.842 | 21.245 | 27.771 | 0.59 | -96.4396 | 70.5742 | [13 empty] | 92 | 277 | 60 | 276.97 | 36.29 | 0.919 | 0.0914 | 25.441 | 21.256 | 27.687 | 0.5885 | -96.4504 | 64.037
89 | 120 | 60 | 119.94 | 27.546 | 0.5371 | 0.1625 | 43.716 | 41.198 | 7.285 | 0.3001 | -99.066 | 55.8741 | [13 empty] | 89 | 277 | 60 | 276.96 | 35.35 | 0.566 | 0.0578 | 21.848 | 41.195 | 7.017 | 0.2891 | -99.1004 | 51.0777 | 89 | 120 | 60 | 119.94 | 30.49 | 0.836 | 0.2285 | 50.434 | 21.245 | 27.762 | 0.5898 | -96.4408 | 70.5502 | [13 empty] | 89 | 277 | 60 | 276.97 | 36.29 | 0.919 | 0.0915 | 23.253 | 21.257 | 27.691 | 0.5886 | -96.4499 | 64.0479
86 | 120 | 60 | 119.94 | 27.553 | 0.5371 | 0.1625 | 35.911 | 41.199 | 7.285 | 0.3001 | -99.066 | 55.8741 | [13 empty] | 86 | 277 | 60 | 276.97 | 35.34 | 0.564 | 0.0576 | 13.054 | 41.196 | 7.016 | 0.289 | -99.1005 | 51.2411 | 86 | 120 | 60 | 119.94 | 30.5 | 0.835 | 0.2284 | 42.803 | 21.245 | 27.761 | 0.5897 | -96.4409 | 70.6228 | [13 empty] | 86 | 277 | 60 | 276.97 | 36.28 | 0.919 | 0.0914 | 18.474 | 21.257 | 27.687 | 0.5884 | -96.4504 | 64.0261
83 | 120 | 60 | 119.94 | 27.543 | 0.5367 | 0.1625 | 33.839 | 41.2 | 7.283 | 0.3001 | -99.0663 | 55.9158 | [13 empty] | 83 | 277 | 60 | 276.96 | 35.34 | 0.568 | 0.058 | 19.919 | 41.197 | 7.016 | 0.289 | -99.1005 | 50.8803 | 83 | 120 | 60 | 119.94 | 30.47 | 0.836 | 0.2286 | 47.691 | 21.246 | 27.756 | 0.5897 | -96.4415 | 70.5383 | [13 empty] | 83 | 277 | 60 | 276.97 | 36.27 | 0.917 | 0.0913 | 25.145 | 21.257 | 27.687 | 0.5885 | -96.4504 | 64.1767
80 | 120 | 60 | 119.94 | 27.543 | 0.5368 | 0.1625 | 34.274 | 41.202 | 7.285 | 0.3001 | -99.066 | 55.9054 | [13 empty] | 80 | 277 | 60 | 276.96 | 35.35 | 0.564 | 0.0576 | 20.546 | 41.198 | 7.016 | 0.289 | -99.1005 | 51.2411 | 80 | 120 | 60 | 119.94 | 30.47 | 0.836 | 0.2287 | 48.136 | 21.246 | 27.749 | 0.5895 | -96.4424 | 70.5144 | [13 empty] | 80 | 277 | 60 | 276.97 | 36.28 | 0.92 | 0.0915 | 18.046 | 21.257 | 27.685 | 0.5885 | -96.4506 | 63.9674
77 | 120 | 60 | 119.94 | 27.553 | 0.5348 | 0.1618 | 44.326 | 41.204 | 7.283 | 0.3001 | -99.0663 | 56.1144 | [13 empty] | 77 | 277 | 60 | 276.96 | 35.34 | 0.563 | 0.0575 | 13.307 | 41.199 | 7.016 | 0.2891 | -99.1005 | 51.3499 | 77 | 120 | 60 | 119.94 | 30.48 | 0.837 | 0.2289 | 41.776 | 21.246 | 27.75 | 0.5895 | -96.4423 | 70.4301 | [13 empty] | 77 | 277 | 60 | 276.97 | 36.27 | 0.916 | 0.0912 | 22.967 | 21.258 | 27.693 | 0.5887 | -96.4496 | 64.2686
74 | 120 | 60 | 119.94 | 27.554 | 0.5373 | 0.1625 | 35.579 | 41.205 | 7.283 | 0.3001 | -99.0663 | 55.8533 | [13 empty] | 74 | 277 | 60 | 276.96 | 35.35 | 0.566 | 0.0578 | 20.086 | 41.201 | 7.015 | 0.289 | -99.1006 | 51.0601 | 74 | 120 | 60 | 119.94 | 30.48 | 0.837 | 0.229 | 47.648 | 21.247 | 27.743 | 0.5894 | -96.4432 | 70.4182 | [13 empty] | 74 | 277 | 60 | 276.97 | 36.25 | 0.918 | 0.0915 | 24.053 | 21.258 | 27.686 | 0.5886 | -96.4505 | 64.1176
71 | 120 | 60 | 119.94 | 27.559 | 0.5354 | 0.162 | 45.735 | 41.206 | 7.283 | 0.3001 | -99.0663 | 56.0516 | [13 empty] | 71 | 277 | 60 | 276.96 | 35.35 | 0.565 | 0.0578 | 21.517 | 41.202 | 7.015 | 0.289 | -99.1006 | 51.1504 | 71 | 120 | 60 | 119.94 | 30.5 | 0.837 | 0.229 | 48.613 | 21.248 | 27.736 | 0.5893 | -96.4441 | 70.4062 | [13 empty] | 71 | 277 | 60 | 276.97 | 36.3 | 0.921 | 0.0916 | 18.672 | 21.259 | 27.687 | 0.5885 | -96.4504 | 63.8979
68 | 120 | 60 | 119.94 | 27.546 | 0.537 | 0.1626 | 34.591 | 41.207 | 7.283 | 0.3001 | -99.0663 | 55.8845 | [13 empty] | 68 | 277 | 60 | 276.97 | 35.34 | 0.563 | 0.0575 | 12.834 | 41.203 | 7.015 | 0.289 | -99.1006 | 51.3321 | 68 | 120 | 60 | 119.94 | 30.5 | 0.837 | 0.229 | 41.515 | 21.248 | 27.731 | 0.5892 | -96.4447 | 70.3943 | [13 empty] | 68 | 277 | 60 | 276.97 | 36.27 | 0.918 | 0.0914 | 23.89 | 21.259 | 27.68 | 0.5884 | -96.4513 | 64.0959
65 | 120 | 60 | 119.94 | 27.557 | 0.5354 | 0.162 | 43.161 | 41.208 | 7.281 | 0.3001 | -99.0665 | 56.0516 | [13 empty] | 65 | 277 | 60 | 276.97 | 35.35 | 0.565 | 0.0577 | 13.007 | 41.204 | 7.014 | 0.289 | -99.1008 | 51.1504 | 65 | 120 | 60 | 119.94 | 30.49 | 0.835 | 0.2283 | 47.293 | 21.248 | 27.728 | 0.5891 | -96.4451 | 70.5509 | [13 empty] | 65 | 277 | 60 | 276.97 | 36.26 | 0.915 | 0.0911 | 23.746 | 21.259 | 27.676 | 0.5883 | -96.4518 | 64.2951
62 | 120 | 60 | 119.94 | 27.548 | 0.5351 | 0.162 | 35.684 | 41.21 | 7.282 | 0.3001 | -99.0664 | 56.083 | [13 empty] | 62 | 277 | 60 | 276.97 | 35.36 | 0.567 | 0.0579 | 13.088 | 41.205 | 7.014 | 0.289 | -99.1008 | 50.97 | 62 | 120 | 60 | 119.94 | 30.47 | 0.835 | 0.2285 | 40.051 | 21.248 | 27.726 | 0.5891 | -96.4454 | 70.5509 | [13 empty] | 62 | 277 | 60 | 276.97 | 36.27 | 0.918 | 0.0914 | 17.966 | 21.259 | 27.671 | 0.5882 | -96.4524 | 64.0741
59 | 120 | 60 | 119.94 | 27.549 | 0.5354 | 0.162 | 34.591 | 41.211 | 7.279 | 0.3 | -99.0668 | 56.0329 | [13 empty] | 59 | 277 | 60 | 276.96 | 35.34 | 0.567 | 0.0579 | 20.419 | 41.206 | 7.013 | 0.289 | -99.1009 | 50.97 | 59 | 120 | 60 | 119.94 | 30.49 | 0.835 | 0.2285 | 47.492 | 21.249 | 27.727 | 0.5891 | -96.4453 | 70.5509 | [13 empty] | 59 | 277 | 60 | 276.97 | 36.26 | 0.919 | 0.0916 | 23.341 | 21.259 | 27.669 | 0.5882 | -96.4527 | 64.0044
56 | 120 | 60 | 119.94 | 27.55 | 0.536 | 0.1622 | 44.649 | 41.212 | 7.281 | 0.3001 | -99.0665 | 55.9888 | [13 empty] | 56 | 277 | 60 | 276.97 | 35.35 | 0.567 | 0.0579 | 12.947 | 41.207 | 7.012 | 0.2889 | -99.101 | 50.9524 | 56 | 120 | 60 | 119.94 | 30.47 | 0.836 | 0.2287 | 41.86 | 21.249 | 27.723 | 0.5891 | -96.4458 | 70.4665 | [13 empty] | 56 | 277 | 60 | 276.97 | 36.28 | 0.92 | 0.0916 | 19.297 | 21.26 | 27.671 | 0.5883 | -96.4524 | 63.9457
53 | 120 | 60 | 119.94 | 27.559 | 0.5354 | 0.162 | 35.587 | 41.213 | 7.279 | 0.3 | -99.0668 | 56.0329 | [13 empty] | 53 | 277 | 60 | 276.96 | 35.35 | 0.567 | 0.0579 | 21.018 | 41.209 | 7.012 | 0.289 | -99.101 | 50.97 | 53 | 120 | 60 | 119.94 | 30.47 | 0.835 | 0.2284 | 48.762 | 21.25 | 27.718 | 0.5889 | -96.4464 | 70.5269 | [13 empty] | 53 | 277 | 60 | 276.97 | 36.28 | 0.918 | 0.0914 | 24.752 | 21.259 | 27.667 | 0.5881 | -96.4529 | 64.0632
50 | 120 | 60 | 119.94 | 27.558 | 0.5374 | 0.1626 | 43.692 | 41.215 | 7.28 | 0.3 | -99.0667 | 55.8243 | [13 empty] | 50 | 277 | 60 | 276.96 | 35.34 | 0.567 | 0.058 | 19.599 | 41.21 | 7.009 | 0.2889 | -99.1014 | 50.9524 | 50 | 120 | 60 | 119.93 | 30.48 | 0.837 | 0.229 | 46.946 | 21.25 | 27.717 | 0.589 | -96.4465 | 70.3704 | [13 empty] | 50 | 277 | 60 | 276.97 | 36.27 | 0.917 | 0.0913 | 24.875 | 21.26 | 27.675 | 0.5883 | -96.4519 | 64.1549
47 | 120 | 60 | 119.94 | 27.555 | 0.5358 | 0.1622 | 46.049 | 41.216 | 7.28 | 0.3 | -99.0667 | 55.991 | [13 empty] | 47 | 277 | 60 | 276.96 | 35.36 | 0.566 | 0.0578 | 21.168 | 41.211 | 7.012 | 0.289 | -99.101 | 51.0601 | 47 | 120 | 60 | 119.94 | 30.49 | 0.835 | 0.2283 | 50.198 | 21.251 | 27.715 | 0.5889 | -96.4468 | 70.5269 | [13 empty] | 47 | 277 | 60 | 276.97 | 36.26 | 0.915 | 0.0912 | 24.29 | 21.26 | 27.674 | 0.5883 | -96.4521 | 64.2951
44 | 120 | 60 | 119.94 | 27.55 | 0.5354 | 0.162 | 35.72 | 41.217 | 7.281 | 0.3001 | -99.0665 | 56.0516 | [13 empty] | 44 | 277 | 60 | 276.97 | 35.35 | 0.564 | 0.0576 | 20.518 | 41.212 | 7.012 | 0.289 | -99.101 | 51.2411 | 44 | 120 | 60 | 119.94 | 30.48 | 0.835 | 0.2283 | 40.778 | 21.251 | 27.712 | 0.5889 | -96.4472 | 70.5269 | [13 empty] | 44 | 277 | 60 | 276.97 | 36.28 | 0.919 | 0.0915 | 23.294 | 21.261 | 27.666 | 0.5882 | -96.4531 | 64.0044
41 | 120 | 60 | 119.94 | 27.561 | 0.5374 | 0.1625 | 44.064 | 41.218 | 7.282 | 0.3001 | -99.0664 | 55.8429 | [13 empty] | 41 | 277 | 60 | 276.96 | 35.36 | 0.568 | 0.058 | 21.344 | 41.213 | 7.013 | 0.289 | -99.1009 | 50.8803 | 41 | 120 | 60 | 119.94 | 30.49 | 0.835 | 0.2282 | 47.483 | 21.251 | 27.707 | 0.5888 | -96.4478 | 70.515 | [13 empty] | 41 | 277 | 60 | 276.97 | 36.27 | 0.919 | 0.0915 | 17.667 | 21.261 | 27.659 | 0.588 | -96.454 | 63.9826
38 | 120 | 60 | 119.94 | 27.549 | 0.5357 | 0.1621 | 45.546 | 41.219 | 7.281 | 0.3001 | -99.0665 | 56.0202 | [13 empty] | 38 | 277 | 60 | 276.96 | 35.36 | 0.565 | 0.0577 | 20.608 | 41.214 | 7.011 | 0.289 | -99.1012 | 51.1504 | 38 | 120 | 60 | 119.94 | 30.47 | 0.835 | 0.2284 | 42.254 | 21.252 | 27.701 | 0.5886 | -96.4486 | 70.491 | [13 empty] | 38 | 277 | 60 | 276.97 | 36.27 | 0.917 | 0.0912 | 23.723 | 21.261 | 27.653 | 0.5879 | -96.4547 | 64.1112
35 | 120 | 60 | 119.94 | 27.553 | 0.5356 | 0.1621 | 35.829 | 41.221 | 7.279 | 0.3001 | -99.0668 | 56.0306 | [13 empty] | 35 | 277 | 60 | 276.97 | 35.35 | 0.563 | 0.0575 | 20.423 | 41.215 | 7.01 | 0.2889 | -99.1013 | 51.3144 | 35 | 120 | 60 | 119.94 | 30.48 | 0.836 | 0.2286 | 43.912 | 21.252 | 27.7 | 0.5886 | -96.4487 | 70.4067 | [13 empty] | 35 | 277 | 60 | 276.97 | 36.27 | 0.918 | 0.0913 | 24.621 | 21.261 | 27.65 | 0.5878 | -96.4551 | 64.0305
32 | 120 | 60 | 119.94 | 27.554 | 0.5365 | 0.1624 | 44.438 | 41.222 | 7.279 | 0.3001 | -99.0668 | 55.9366 | [13 empty] | 32 | 277 | 60 | 276.97 | 35.35 | 0.563 | 0.0575 | 20.708 | 41.216 | 7.009 | 0.2889 | -99.1014 | 51.3144 | 32 | 120 | 60 | 119.94 | 30.5 | 0.837 | 0.2288 | 43.158 | 21.253 | 27.698 | 0.5886 | -96.449 | 70.3226 | [13 empty] | 32 | 277 | 60 | 276.97 | 36.26 | 0.917 | 0.0914 | 18.477 | 21.262 | 27.652 | 0.5879 | -96.4549 | 64.1112
29 | 120 | 60 | 119.94 | 27.561 | 0.5368 | 0.1624 | 35.678 | 41.223 | 7.278 | 0.3 | -99.0669 | 55.8867 | [13 empty] | 29 | 277 | 60 | 276.97 | 35.35 | 0.565 | 0.0577 | 21.826 | 41.217 | 7.008 | 0.2889 | -99.1015 | 51.1327 | 29 | 120 | 60 | 119.94 | 30.48 | 0.836 | 0.2288 | 42.445 | 21.253 | 27.703 | 0.5887 | -96.4483 | 70.4187 | [13 empty] | 29 | 277 | 60 | 276.97 | 36.27 | 0.916 | 0.0911 | 24.99 | 21.262 | 27.65 | 0.5878 | -96.4551 | 64.1703
26 | 120 | 60 | 119.94 | 27.564 | 0.5357 | 0.162 | 44.373 | 41.225 | 7.279 | 0.3001 | -99.0668 | 56.0202 | [13 empty] | 26 | 277 | 60 | 276.96 | 35.36 | 0.568 | 0.058 | 20.742 | 41.218 | 7.008 | 0.2889 | -99.1015 | 50.8627 | 26 | 120 | 60 | 119.94 | 30.49 | 0.837 | 0.229 | 42.156 | 21.253 | 27.705 | 0.5888 | -96.4481 | 70.3465 | [13 empty] | 26 | 277 | 60 | 276.97 | 36.27 | 0.918 | 0.0913 | 18.051 | 21.262 | 27.627 | 0.5873 | -96.4581 | 63.976
23 | 120 | 60 | 119.94 | 27.558 | 0.5358 | 0.1621 | 43.481 | 41.226 | 7.279 | 0.3001 | -99.0668 | 56.0097 | [13 empty] | 23 | 277 | 60 | 276.96 | 35.34 | 0.565 | 0.0577 | 21.222 | 41.219 | 7.009 | 0.2889 | -99.1014 | 51.1327 | 23 | 120 | 60 | 119.94 | 30.49 | 0.836 | 0.2287 | 47.709 | 21.254 | 27.704 | 0.5888 | -96.4482 | 70.4306 | [13 empty] | 23 | 277 | 60 | 276.97 | 36.28 | 0.915 | 0.0911 | 24.802 | 21.262 | 27.645 | 0.5877 | -96.4558 | 64.2295
20 | 120 | 60 | 119.94 | 27.534 | 0.5362 | 0.1624 | 42.982 | 41.227 | 7.279 | 0.3001 | -99.0668 | 55.9679 | [13 empty] | 20 | 277 | 60 | 276.97 | 35.34 | 0.564 | 0.0576 | 20.516 | 41.219 | 7.008 | 0.2888 | -99.1015 | 51.2057 | 20 | 120 | 60 | 119.94 | 30.46 | 0.836 | 0.2288 | 40.511 | 21.254 | 27.702 | 0.5888 | -96.4485 | 70.4306 | [13 empty] | 20 | 277 | 60 | 276.97 | 36.24 | 0.916 | 0.0912 | 18.802 | 21.263 | 27.639 | 0.5877 | -96.4565 | 64.1594
17 | 120 | 60 | 119.94 | 27.563 | 0.5353 | 0.162 | 35.361 | 41.228 | 7.279 | 0.3001 | -99.0668 | 56.062 | [13 empty] | 17 | 277 | 60 | 276.97 | 35.34 | 0.563 | 0.0575 | 20.392 | 41.22 | 7.008 | 0.2889 | -99.1015 | 51.3144 | 17 | 120 | 60 | 119.94 | 30.48 | 0.835 | 0.2285 | 41.925 | 21.254 | 27.701 | 0.5887 | -96.4486 | 70.503 | [13 empty] | 17 | 277 | 60 | 276.97 | 36.27 | 0.919 | 0.0915 | 24.195 | 21.263 | 27.638 | 0.5876 | -96.4567 | 63.9391
14 | 120 | 60 | 119.94 | 27.561 | 0.5371 | 0.1625 | 44.243 | 41.229 | 7.278 | 0.3001 | -99.0669 | 55.8741 | [13 empty] | 14 | 277 | 60 | 276.96 | 35.35 | 0.563 | 0.0575 | 21.272 | 41.221 | 7.007 | 0.2888 | -99.1017 | 51.2966 | 14 | 120 | 60 | 119.94 | 30.48 | 0.836 | 0.2287 | 49.079 | 21.254 | 27.699 | 0.5887 | -96.4488 | 70.4187 | [13 empty] | 14 | 277 | 60 | 276.97 | 36.25 | 0.92 | 0.0916 | 18.004 | 21.263 | 27.634 | 0.5875 | -96.4572 | 63.8587
11 | 120 | 60 | 119.94 | 27.562 | 0.535 | 0.1619 | 34.8 | 41.23 | 7.277 | 0.3 | -99.0671 | 56.0748 | [13 empty] | 11 | 277 | 60 | 276.97 | 35.34 | 0.567 | 0.0579 | 13.469 | 41.223 | 7.006 | 0.2888 | -99.1018 | 50.9347 | 11 | 120 | 60 | 119.94 | 30.48 | 0.836 | 0.2288 | 41.862 | 21.255 | 27.701 | 0.5887 | -96.4486 | 70.4187 | [13 empty] | 11 | 277 | 60 | 276.97 | 36.26 | 0.92 | 0.0916 | 22.967 | 21.263 | 27.637 | 0.5876 | -96.4568 | 63.8696
8 | 120 | 60 | 119.94 | 27.572 | 0.5354 | 0.1619 | 35.937 | 41.231 | 7.277 | 0.3001 | -99.0671 | 56.0516 | [13 empty] | 8 | 277 | 60 | 276.97 | 35.35 | 0.566 | 0.0578 | 13.203 | 41.223 | 7.008 | 0.2889 | -99.1015 | 51.0424 | 8 | 120 | 60 | 119.94 | 30.5 | 0.835 | 0.2282 | 47.26 | 21.255 | 27.694 | 0.5886 | -96.4495 | 70.491 | [13 empty] | 8 | 277 | 60 | 276.97 | 36.27 | 0.917 | 0.0912 | 19.423 | 21.263 | 27.632 | 0.5875 | -96.4574 | 64.0676
5 | 120 | 60 | 119.94 | 27.554 | 0.5352 | 0.1619 | 34.487 | 41.233 | 7.277 | 0.3001 | -99.0671 | 56.0725 | [13 empty] | 5 | 277 | 60 | 276.97 | 35.34 | 0.564 | 0.0577 | 13.716 | 41.224 | 7.008 | 0.2889 | -99.1015 | 51.2234 | 5 | 120 | 60 | 119.94 | 30.49 | 0.835 | 0.2284 | 42.315 | 21.255 | 27.693 | 0.5886 | -96.4496 | 70.491 | [13 empty] | 5 | 277 | 60 | 276.97 | 36.26 | 0.917 | 0.0913 | 23.097 | 21.263 | 27.636 | 0.5876 | -96.4569 | 64.0785
2 | 120 | 60 | 119.94 | 27.562 | 0.5362 | 0.1622 | 43.607 | 41.234 | 7.277 | 0.3001 | -99.0671 | 55.9679 | [13 empty] | 2 | 277 | 60 | 276.97 | 35.35 | 0.566 | 0.0579 | 13.113 | 41.225 | 7.008 | 0.2889 | -99.1015 | 51.0424 | 2 | 120 | 60 | 119.94 | 30.47 | 0.835 | 0.2283 | 46.553 | 21.256 | 27.692 | 0.5886 | -96.4497 | 70.491 | [13 empty] | 2 | 277 | 60 | 276.97 | 36.27 | 0.918 | 0.0914 | 18.831 | 21.264 | 27.636 | 0.5876 | -96.4569 | 64.0087
0 | 120 | 60 | 119.94 | 25.169 | 0.076 | 0.0252 | 10.276 | 37.787 | 0.0542 | 0.00186 | -99.9931 | 2.4474 | [13 empty] | 0 | 277 | 60 | 276.97 | 34.74 | 0.244 | 0.0254 | 8.559 | 37.793 | 0.053 | 0.00183 | -99.9932 | 0.75 | 0 | 120 | 60 | 119.94 | 25.191 | 0.076 | 0.025 | 10.185 | 18.756 | 0.0365 | 0.00059 | -99.9953 | 0.77632 | [13 empty] | 0 | 277 | 60 | 276.97 | 34.76 | 0.243 | 0.0253 | 8.026 | 18.759 | 0.0358 | 0.00058 | -99.9954 | 0.23868

## RSET Dimming
RSET Dimming
DER-925 Unit 9
48V LED, 120 VAC | [12 empty] | 46V LED, 230 VAC | [12 empty] | 48V LED, 277 VAC | [12 empty] | 24V LED, 120 VAC | [12 empty] | 24V LED, 230 VAC | [12 empty] | 24V LED, 277 VAC
| Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement | [5 empty] | Input |  | Input Measurement |  |  |  |  | Output 1 Measurement
| Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency |  | Vac (rms) | Freq (Hz) | Vin (rms) | Iin (mA) | Pin (W) | PF | % THD | Vo (V) | Io (mA) | Po (W) | %I Reg | Efficiency
3 | 120 | 60 | 119.88 | 352.26 | 41.872 | 0.9915 | 4.136 | 47.939 | 773.9 | 37.064 | -0.78205 | 88.5174 | [13 empty] | 3 | 277 | 60 | 276.85 | 166.35 | 41.561 | 0.9024 | 9.951 | 47.893 | 773.9 | 37.027 | -0.78205 | 89.0907 | 3 | 120 | 60 | 119.81 | 181.49 | 21.22 | 0.9759 | 4.947 | 23.868 | 771.9 | 18.405 | -1.0385 | 86.7342 | [13 empty] | 3 | 277 | 60 | 276.9 | 101.23 | 21.457 | 0.7655 | 16.78 | 23.878 | 772.3 | 18.419 | -0.98718 | 85.8415
6 | 120 | 60 | 119.89 | 352.47 | 41.89 | 0.9915 | 4.377 | 47.952 | 774 | 37.079 | -0.76923 | 88.5152 | [13 empty] | 6 | 277 | 60 | 276.85 | 166.49 | 41.599 | 0.9025 | 9.093 | 47.907 | 774.2 | 37.05 | -0.74359 | 89.0646 | 6 | 120 | 60 | 119.82 | 181.61 | 21.235 | 0.9759 | 5.774 | 23.877 | 772 | 18.414 | -1.0256 | 86.7153 | [13 empty] | 6 | 277 | 60 | 276.9 | 101.17 | 21.438 | 0.7653 | 17.753 | 23.874 | 771.9 | 18.407 | -1.0385 | 85.8616
9 | 120 | 60 | 119.77 | 257.54 | 30.468 | 0.9877 | 4.159 | 46.859 | 577.06 | 27.013 | -26.0179 | 88.6602 | [13 empty] | 9 | 277 | 60 | 276.87 | 128.44 | 30.227 | 0.8501 | 12.093 | 46.797 | 573.26 | 26.8 | -26.5051 | 88.6625 | 9 | 120 | 60 | 119.85 | 133.5 | 15.34 | 0.9587 | 5.145 | 23.38 | 570.01 | 13.312 | -26.9218 | 86.7797 | [13 empty] | 9 | 277 | 60 | 276.91 | 83.24 | 15.674 | 0.68 | 21.861 | 23.394 | 572.95 | 13.388 | -26.5449 | 85.4153
12 | 120 | 60 | 119.82 | 190.75 | 22.376 | 0.9791 | 3.43 | 45.96 | 430.98 | 19.785 | -44.7462 | 88.4206 | [13 empty] | 12 | 277 | 60 | 276.89 | 104.43 | 22.717 | 0.7855 | 15.398 | 45.955 | 435.53 | 19.994 | -44.1628 | 88.0134 | 12 | 120 | 60 | 119.88 | 101.75 | 11.374 | 0.9325 | 6.252 | 22.997 | 429.01 | 9.854 | -44.9987 | 86.6362 | [13 empty] | 12 | 277 | 60 | 276.92 | 71.21 | 11.683 | 0.5925 | 25.225 | 23.009 | 430.59 | 9.896 | -44.7962 | 84.7043
15 | 120 | 60 | 119.84 | 152.26 | 17.662 | 0.9682 | 5.028 | 45.372 | 343.1 | 15.55 | -56.0128 | 88.0421 | [13 empty] | 15 | 277 | 60 | 276.91 | 89.85 | 17.925 | 0.7206 | 18.58 | 45.356 | 345.51 | 15.657 | -55.7038 | 87.3473 | 15 | 120 | 60 | 119.89 | 83.79 | 9.05 | 0.901 | 7.622 | 22.746 | 343.87 | 7.813 | -55.9141 | 86.3315 | [13 empty] | 15 | 277 | 60 | 276.92 | 64.47 | 9.366 | 0.5246 | 28.344 | 22.76 | 345.91 | 7.864 | -55.6526 | 83.9633
18 | 120 | 60 | 119.86 | 128.46 | 14.734 | 0.9571 | 4.29 | 44.974 | 287.93 | 12.937 | -63.0859 | 87.8037 | [13 empty] | 18 | 277 | 60 | 276.91 | 80.98 | 14.919 | 0.6654 | 21.497 | 44.945 | 288.12 | 12.938 | -63.0615 | 86.7216 | 18 | 120 | 60 | 119.89 | 72.09 | 7.48 | 0.8654 | 9.027 | 22.561 | 285.52 | 6.434 | -63.3949 | 86.016 | [13 empty] | 18 | 277 | 60 | 276.92 | 60 | 7.812 | 0.4702 | 30.693 | 22.576 | 288.05 | 6.496 | -63.0705 | 83.1541
21 | 120 | 60 | 119.87 | 110.32 | 12.491 | 0.9445 | 4.808 | 44.763 | 244.49 | 10.933 | -68.6551 | 87.527 | [13 empty] | 21 | 277 | 60 | 276.91 | 74.8 | 12.806 | 0.6183 | 23.371 | 44.752 | 246.69 | 11.03 | -68.3731 | 86.1315 | 21 | 120 | 60 | 119.9 | 64.447 | 6.4316 | 0.8324 | 12.842 | 22.547 | 244.98 | 5.5172 | -68.5923 | 85.7827 | [13 empty] | 21 | 277 | 60 | 276.93 | 56.86 | 6.711 | 0.4262 | 32.262 | 22.555 | 245.36 | 5.5288 | -68.5436 | 82.3841
24 | 120 | 60 | 119.88 | 97.91 | 10.915 | 0.9303 | 5.169 | 44.501 | 214.19 | 9.523 | -72.5397 | 87.2469 | [13 empty] | 24 | 277 | 60 | 276.92 | 70.23 | 11.217 | 0.5768 | 25.993 | 44.487 | 215.78 | 9.591 | -72.3359 | 85.5041 | 24 | 120 | 60 | 119.9 | 58.665 | 5.5933 | 0.7952 | 14.692 | 22.417 | 213.36 | 4.7771 | -72.6462 | 85.4075 | [13 empty] | 24 | 277 | 60 | 276.93 | 54.94 | 5.915 | 0.3888 | 33.596 | 22.431 | 215.18 | 4.8222 | -72.4128 | 81.5249
27 | 120 | 60 | 119.88 | 90.64 | 9.978 | 0.9184 | 5.778 | 44.334 | 195.54 | 8.659 | -74.9308 | 86.7809 | [13 empty] | 27 | 277 | 60 | 276.92 | 67.26 | 10.19 | 0.5471 | 27.597 | 44.31 | 195.75 | 8.665 | -74.9038 | 85.0343 | 27 | 120 | 60 | 119.91 | 55.37 | 5.1092 | 0.7696 | 13.42 | 22.338 | 195.12 | 4.353 | -74.9846 | 85.1992 | [13 empty] | 27 | 277 | 60 | 276.93 | 53.85 | 5.401 | 0.3622 | 34.535 | 22.346 | 195.5 | 4.3643 | -74.9359 | 80.8054
30 | 120 | 60 | 119.88 | 90.55 | 9.973 | 0.9184 | 5.93 | 44.334 | 195.53 | 8.659 | -74.9321 | 86.8244 | [13 empty] | 30 | 277 | 60 | 276.92 | 67.25 | 10.189 | 0.5471 | 27.094 | 44.312 | 195.77 | 8.667 | -74.9013 | 85.0623 | 30 | 120 | 60 | 119.91 | 55.383 | 5.1097 | 0.7694 | 13.647 | 22.339 | 195.1 | 4.3529 | -74.9872 | 85.189 | [13 empty] | 30 | 277 | 60 | 276.93 | 53.82 | 5.399 | 0.3623 | 34.584 | 22.347 | 195.47 | 4.3639 | -74.9397 | 80.8279

## EMI
EMI Scan
DER-925 Unit 9
| 115VAC EMI Scan | 115VAC EMI Table
| 230VAC EMI Scan | 230VAC EMI Table